SUNDIAL ENGINEERING & SURVEY

4720 South Rainbow Boulevard, Suite 210 · Las Vegas, Nevada 89103 · (702) 555-0142 · NV COA #C-3874

MEMORANDUM

| TO: | Garrett Nokes, Vice President, Land Development — Callaway Land Partners 8880 W. Sunset Road, Suite 400, Las Vegas, NV 89148 |
| --- | --- |
| FROM: | Max Braddock, Project Manager — Sundial Engineering & Survey |
| DATE: | 10/31/2026 |
| CC: | Lee Chastain, Callaway Land Partners · Jonathan R. Kessler, PE, Principal-in-Charge and Engineer of Record · Priya Sarwal, EIT, Grading and Drainage Lead · Sundial Drainage Lead (owner, comment G-4) · Project File 2201-03 |
| RE: | Desert Sage Ranch Phase 3 — IP-26-100288 / FM-26-100290 — Clark County Public Works Comment G-4 (letter of 10/09/2026): Emergency Spillway, Sheet C-9 — Adequacy and Disposition |

1.  Purpose and Bottom Line

Public Works comment G-4 (Dale Yeoman, PE, Ph3 Comments, 10/09/2026) reads: “The emergency spillway shown on Sheet C-9 lacks freeboard dimensioning and downstream apron details. Provide sizing calculations, spillway section, and erosion protection consistent with the RFCD Hydrologic Criteria and Drainage Design Manual.” Before the response is assigned, we checked the spillway as drawn against the Phase 3 improvement plans and our internal QA/QC checklist, the District-accepted Master Drainage Study (MDS) and the Phase 3 storm drain worksheets, and the Phase 2 plan check comments and the Flood Control District’s acceptance letter. Records and their short names are listed in Attachment C.

The spillway as drawn does not hold up. Before the berm overtops it can pass 30.454425 cfs — 34.450707 % of the 88.4 cfs it must carry — and whatever it does pass lands on two residential lots. The fix stays inside the accepted MDS, so it does not go back to the District and does not move the schedule. One disposition per question follows; findings are in Sections 3 through 6, the arithmetic in Attachment A, and draft sheet language in Attachment B. Elevations are feet, NAVD 88 (C-1, Datum note).

2.  Dispositions

| No. | Question | Disposition |
| --- | --- | --- |
| 1 | Can we answer G-4 with what is on Sheet C-9 today? | No. There is no sizing anywhere in the record; the C-9 freeboard figures are wrong; the spillway passes 30.454425 cfs of the 88.4 cfs design discharge before the berm overtops; the apron stops short of the toe; and the outlet as detailed does not reproduce the rating behind the 100-year water surface. The spillway is redesigned and C-9 and C-6 are reissued (Section 3). |
| 2 | Do the revisions trigger an amendment to the accepted Master Drainage Study? | No. The revisions directed here hold every District-accepted parameter — 6.4 ac-ft allocation, 78 cfs shared-outfall cap, 40.0 ac at 42 % impervious, 88.4 cfs inflow, the App. D-2 rating through the 2,858.50-ft crest, basin in Parcel E. The 09/25/2026 preliminary detention calculation departs from all of them, would trigger an amendment, and is set aside (Section 4). |
| 3 | What do the spillway detail and basin notes say on the revised C-9? | Spillway moved to the south berm; crest held at 2,858.50 ft; crest lengthened from 20.0 ft to 50.0 ft; design discharge 88.4 cfs with the outlet blocked; design water surface 2,859.27 ft; top of berm raised 1.10 ft to 2,860.30 ft for 1.03 ft of freeboard; armor carried over the full face into a lined overflow channel; outlet works conformed to MDS App. D-2; freeboard dimensioned; basin notes corrected and the allocation cited (Section 5; Attachment B). |
| 4 | Where does the overflow end up once it leaves the berm? | Today: on private Lots 51 and 57. On the revised C-9 it leaves the south berm, runs in a lined channel on HOA land and a drainage easement to the Windmill Lane right-of-way, and flows west in Windmill Lane to the regional system at the southwest corner. It crosses no lot (Section 6). |

Schedule. The redesign needs no District re-review, so it fits the dates already set: revised sheets to me by 11/13/2026 (10/09/2026 coordination e-mail), internal completion 11/22/2026 and resubmittal 11/30/2026 (Tracker). Two things would put the 12/18/2026 recordation at risk: carrying the preliminary calculation into the resubmittal, which is a formal amendment with District re-review before plan approval (FCD Acceptance Letter; TM COA Condition 2), or moving the Parcel E line to make room for the raised berm, which is a significant change requiring Town Advisory Board and Planning Commission hearings (TM COA Conditions 14 and 15). This memo rules out both.

3.  The Spillway as Drawn

3.1  No sizing exists anywhere in the record. The C-9 spillway detail gives no design discharge — only “routing check under storm exceeding 100-year, 24-hour input.” MDS App. D-2 stops at the crest (2,858.50 ft, 7.12 ac-ft, 41.5 cfs of outlet-works discharge) and shows no discharge at the 2,859.20-ft top of berm. Neither the Hydrology Worksheet nor the HGL Worksheet contains a spillway rating. There is no calculation on file to give Public Works.

3.2  The C-9 freeboard figures contradict the sheet’s own elevations. With the 100-year water surface at 2,857.91 ft, the crest at 2,858.50 ft and the top of berm at 2,859.20 ft (C-6; C-9), the crest is 0.59 ft above the 100-year water surface. The C-9 spillway detail says 0.71 ft and the C-9 Basin Notes say 0.60 ft. The 0.70-ft crest-to-berm and 1.29-ft water-surface-to-berm figures are correct, but the 1.29 ft applies only with the outlet working and says nothing about freeboard while the spillway runs — which is what G-4 asks us to dimension (Attachment A-1).

3.3  The spillway carries about one-third of its design flow before the berm overtops. We size an emergency spillway on the standard basis — the 100-year peak inflow with the outlet works blocked — which is 88.4 cfs for Phase 3 (MDS App. C-2 and D-1; Hydrology Worksheet, Peak Flows tab, cell B13). With 0.70 ft of head between crest and berm, the 20.0-ft broad-crested weir (C-6; C-9) passes 30.454425 cfs at C = 2.6 ft0.5/s, 34.450707 % of the design discharge. Even at the theoretical ceiling for a broad crest, C = 3.088809 ft0.5/s, it passes 36.179962 cfs, 40.927559 %. Carrying 88.4 cfs over the 20.0-ft crest takes 1.424402 ft of head — a water surface of 2,859.924402 ft, 0.724402 ft over the berm. That holds even if no freeboard were required at all (Attachment A-2).

3.4  No crest length produces freeboard with the berm where it is. The record’s minimum freeboard is 1.0 ft (C-9 Basin Notes), and on Phase 2 Public Works required it “above the design HGL” and dimensioned (Ph2 Comments, G-3, 09/28/2022, resolved 12/14/2022; Ph2 Response Matrix, 11/07/2022). For the spillway the design water surface is the crest plus the design head, so with the crest held at 2,858.50 ft the berm must stand at 2,859.50 ft plus the head. The 2,859.20-ft berm is at least 0.30 ft short however long the crest is made. The berm has to go up (Attachment A-3).

3.5  The apron stops short of the toe and is not detailed. C-9 calls for a 15-ft by 20-ft grouted riprap apron, D50 = 12 in, “extending from weir toe to natural grade beyond the berm at elevation 2,853.00′.” The 5.50-ft fall from the crest to 2,853.00 ft on the 3H:1V exterior slope (C-6) runs 16.50 ft horizontally and 17.392527 ft along the slope. Read as starting at the downstream edge of the 6.0-ft crest, the 15-ft apron ends 1.50 ft (horizontal) short of the toe and never reaches natural grade; read as starting at the toe, it leaves the 17.392527-ft face unarmored. Either way the face-to-grade transition, where the energy is dissipated, is unprotected. No layer thickness, bedding, filter, toe-down or edge key is shown, and there is no spillway section (Attachment A-5).

3.6  The outlet as detailed does not reproduce the rating behind the 100-year water surface. The crest’s 0.59-ft margin rests on the 2,857.91-ft water surface routed through the MDS App. D-2 rating, which describes orifice-and-weir outlet works. C-9 details a single 12-in by 18-in orifice (centroid 2,851.50 ft) and no weir. At Cd = 0.60 (dimensionless) it releases 80.524019 % more than App. D-2 at 2,853.00 ft and 34.459424 % less at 2,857.91 ft (18.285821 cfs against 27.9 cfs), and it cannot release the accepted 27.9-cfs peak at any stage below the crest (19.108846 cfs at 2,858.50 ft against 41.5 cfs); matching 27.9 cfs at 2,857.91 ft would take Cd = 0.915463, which no orifice plate achieves. Neither the 2,857.91-ft water surface nor the 0.59-ft margin is demonstrated for the outlet as drawn. Public Works required the same reconciliation of the Phase 2 outlet detail (Ph2 Comments, G-2); it closes in the same revision (Attachment A-6).

3.7  Our worksheets and checklist do not support the detail. The HGL Worksheet (Inputs, cell B40) bounds its tailwater check at 2,858.50 ft as “the highest water surface the basin can physically hold”; with the spillway flowing the water surface is the crest plus the head, so that bound is low. The same workbook (Pipe Schedule notes) relies on “the grouted rip-rap apron detailed on Sheet C-9” to take the 14.25-fps Line B discharge at S-15, which enters at the basin’s north face (Inputs, cell B36); that apron belongs to the spillway, on the outside of the east berm. The QA/QC Checklist (08/18/2026, Tab 3) cleared item 27 (spillway) on crest-elevation agreement only, item 28 on freeboard “matching,” item 29 for a “basin outlet swale section” keyed to Section B-B/C-9 — which is the transverse basin section; C-9 has no swale section — and item 26 by matching an orifice “diameter” (the C-9 orifice is a 12-in by 18-in rectangle) to an “inflow-outflow rating” the HGL Worksheet does not contain. None of those items tested capacity, the freeboard arithmetic or the overflow path, so the checklist’s “no open items in Tab 3” cannot be cited in the response.

Disposition 1 — No. G-4 cannot be answered with a narrative or a calculation against Sheet C-9 as it stands. The spillway, apron, outlet works and basin notes are redesigned and C-9 and C-6 are reissued. The drainage lead’s assignment is the redesign defined in Sections 5 and 6, not a response letter.

4.  Amendment to the Accepted Master Drainage Study

The MDS fixes the Phase 3 allocation at 6.4 ac-ft (Table 4-1) and the shared-outfall cap at Q100 ≤ 78 cfs (§5.2), and requires formal amendment and District re-review for any change to the allocations, outfall allowance, tributary breakdown or phase boundaries (§4.4; §7.3). The FCD Acceptance Letter (02/28/2022) names the triggers: “any proposed revision of phase tributary area, impervious cover assumption, hydrologic methodology, storage-indication input, phase boundary, detention basin location, or shared outfall discharge cap.” TM COA Condition 2 separately sends any deviation from District-accepted parameters back to the District before plan approval. At pre-application, Public Works confirmed that a plan set matching the study’s volumes and outfall configuration needs no new hydrology submittal to the District (Pre-App Notes, 06/22/2026, §3.2).

| Parameter | Accepted MDS (source) | Revised C-9 (this memo) | Preliminary calc, 09/25/2026 (cell) |
| --- | --- | --- | --- |
| Criteria manual edition | In effect at MDS preparation (MDS §1.4, §3.1) | Same | “Current” (Inputs B18) |
| 100-yr, 6-hr rainfall | 2.38 in (MDS §3.1) | 2.38 in | 2.42 in (Inputs C25) |
| Phase 3 tributary area | 40.0 ac (Table 4-1) | 40.0 ac | 66.5 ac, incl. 26.5 ac offsite (Detention Sizing B7) |
| Impervious cover | 42 % (Table 4-1) | 42 % | 65 % (Inputs B30) |
| Peak inflow to basin | 88.4 cfs, routed 6-hr peak (App. C-2, D-1) | 88.4 cfs — spillway design discharge | 32.1 cfs, 24-hr composite (Detention Sizing B9); 128.0 cfs, sum of 6-hr sub-basin peaks (Sub-basin Peak Flows G10) |
| Peak outflow | 27.9 cfs (App. D-1) | 27.9 cfs — outlet conformed to App. D-2 | 6.0 cfs “Phase 3 share” (Detention Sizing B15–B16) |
| Storage at 100-yr WSEL | 6.4 ac-ft at 2,857.91 ft (Table 4-1; App. D-2) | 6.40 ac-ft at 2,857.91 ft | 8.1 ac-ft (Detention Sizing C41) |
| Rating at and below crest | App. D-2, through 2,858.50 ft | Unchanged | Not used |
| Basin location | Parcel E (App. E) | Parcel E | Unspecified single basin (Inputs B20) |
| Shared outfall | 78 cfs cap, site-wide; no phase-specific release (§5.2–§5.3) | Unchanged | Computes a phase-specific release, which §5.3 says phase plans shall not do |

Apart from bringing the outlet into line with App. D-2, everything the revision changes lies above the crest or outside the routing: spillway location and length, berm height, armor and overflow channel. The 100-year routing peaks at 2,857.91 ft, 0.59 ft below the crest, so neither the spillway rating nor the added berm height enters it; the App. D-2 top-of-berm row (2,859.20 ft) carries no discharge. Conforming the outlet to App. D-2 restores the accepted storage-indication input rather than departing from it. The overflow route is not a design-storm outfall: with the outlet working the spillway does not flow in the 100-year storm, and the site still discharges through the one shared outfall at no more than 78 cfs (MDS §5.1–§5.2).

The preliminary calculation is the opposite case. It changes the manual, rainfall, tributary area, impervious cover and release rate and arrives at 8.1 ac-ft — 1.7 ac-ft (26.5625 %) over the 6.4 ac-ft allocation, and 0.078545 ac-ft more than the basin holds at today’s top of berm (8.02 ac-ft on the C-9 Storage Summary Table; 8.021455 ac-ft recomputed from its contour areas, Attachment A-7). Its 65 % impervious figure conflicts with the plan set (C-1 General Notes, approximately 42 %) and the Hydrology Worksheet (42 % area-weighted); its 26.5 ac of offsite area conflicts with MDS §2.3, which brings offsite flow in through Phase 1; and nothing in the MDS supports a 6.0-cfs Phase 3 release.

Disposition 2 — No amendment. The C-9 revisions in this memo stay inside the accepted MDS and go to Public Works in the normal resubmittal, with the G-3/G-4 response stating the reconciliation in the terms Public Works set at pre-application. That is also the basis for closing Tracker Outstanding Item 8 (no change to the accepted Phase 3 allocation). The 09/25/2026 preliminary detention calculation is not cited, not used for the C-9 revision and not transmitted.

5.  The Revised Sheet C-9

5.1  Design basis (stated on the sheet and in the calculation package)

Design discharge 88.4 cfs, the Phase 3 100-year peak inflow (MDS App. C-2 and D-1; Hydrology Worksheet B13), with the outlet works fully blocked and the basin at the crest when the peak arrives; no credit for storage or outlet discharge. Hydrology is taken from the MDS unchanged.

Broad-crested weir, Q = C L H1.5, with C = 2.6 ft0.5/s, at the low end of the range used for broad crests and below the 3.088809 ft0.5/s theoretical ceiling; a higher coefficient from the manual table only adds margin. The notch side slopes add capacity that is not counted.

Freeboard of at least 1.0 ft above the spillway design water surface (C-9 Basin Notes minimum; Ph2 Comments G-3).

Crest held at 2,858.50 ft (MDS App. D-2). Lowering it would change an accepted App. D-2 value and shrink the 0.59-ft margin above the 100-year water surface.

5.2  Spillway detail — values

| Item | Revised value | Basis |
| --- | --- | --- |
| Location | South berm, discharging south toward Windmill Lane (was east berm) | Section 6 |
| Crest elevation | 2,858.50 ft (unchanged) | MDS App. D-2; C-9 |
| Crest length | 50.0 ft (was 20.0 ft) | Attachment A-4 |
| Crest breadth | 6.0 ft (unchanged); H/b = 0.128881 (dimensionless), within the broad-crested range | C-9; A-4 |
| Design discharge | 88.4 cfs, outlet works blocked | MDS App. C-2, D-1 |
| Design head | 0.773284 ft (sheet value 0.77 ft) | A-4 |
| Spillway design water surface | 2,859.273284 ft (sheet value 2,859.27 ft) | A-4 |
| Top of berm (minimum rim) | 2,860.30 ft — raised 1.10 ft from 2,859.20 ft | A-4 |
| Freeboard, spillway flowing | 1.026716 ft (sheet value 1.03 ft) ≥ 1.0 ft | A-4 |
| Freeboard, 100-yr WSEL to top of berm | 2.39 ft ≥ 1.0 ft | A-4 |
| Crest above 100-yr WSEL | 0.59 ft | A-1 |
| Discharge with water at top of berm | 313.943944 cfs — 3.551402 times the design discharge | A-4 |
| Notch | 4H:1V side slopes from crest to 2,860.30 ft; top width 64.40 ft | A-4 |
| Unit discharge on exterior face | 1.768 cfs/ft — input to the riprap calculation | A-4 |

Dimension string for the spillway section: basin bottom 2,851.00 ft — 6.91 ft — 100-yr WSEL 2,857.91 ft — 0.59 ft — crest 2,858.50 ft — 0.77 ft — spillway design water surface 2,859.27 ft — 1.03 ft — top of berm 2,860.30 ft.

5.3  Spillway detail — section and erosion protection

The detail carries (a) a section perpendicular to the crest showing the 4H:1V interior slope, the 6.0-ft crest, the 3H:1V exterior face, the armor layers, geotextile and toe-down; (b) a section along the crest showing the notch; and (c) a profile of the overflow channel to Windmill Lane. Armor type stays as drawn — articulated concrete block on the crest and grouted riprap, D50 = 12 in, on the face — and runs continuously across the full 64.40-ft notch, down the full exterior face past the toe, and through the overflow channel to the Windmill Lane right-of-way, with keyed edges and a cutoff at the downstream end. Layer thickness, bedding or filter, toe-down depth and stone size are set by a CCRFCD-manual calculation at 1.768 cfs/ft on the 3H:1V face and dimensioned on the section. No fence, gate, wall, tree or structure is placed across the crest or the channel.

5.4  Basin notes

The Basin Notes are rewritten as in Attachment B. They cite the 6.4 ac-ft allocation by study title, revision, table and acceptance date against the 6.40 ac-ft provided (which also answers G-3); state that the outlet works reproduce the App. D-2 rating; give 2.39 ft of freeboard with the outlet working and 1.03 ft with the spillway flowing; set a 2,860.30-ft minimum rim within Parcel E; define the overflow path and bar overflow onto any lot; and assign Association maintenance, with Parcel E added to CC&R Exhibit B and inspection after any event that reaches the crest. The 0.60-ft and 0.71-ft figures, the 1.29-ft freeboard note and the “open swale” note come off the sheet.

5.5  Consequential edits in the same revision

Footprint. Each 1.00 ft of raise widens the embankment 7.00 ft per side (4H:1V inside plus 3H:1V outside); the 1.10-ft raise adds 7.70 ft per side (Attachment A-8). C-6 and C-9 do not dimension the berm crest or toe, and the FM Check Print does not dimension Parcel E (2.04 ac), so the fit is confirmed on the plotted base. If it is tight, the adjustment is a longer crest — the required berm falls toward the 2,859.50-ft floor (Attachment A-4) — never a lower crest and never a move of the Parcel E line.

C-6 callouts (spillway location and length, top of berm, area at top of berm); C-9 Sections A-A′ and B-B′; the Storage Summary Table extended to 2,860.30 ft, with every value at and below 2,858.50 ft unchanged.

Outlet headwall top raised to 2,860.30 ft. C-9 now calls the headwall 4 ft tall while dimensioning it from a 2,850.00-ft footing to a 2,859.20-ft top (9.20 ft); both are corrected.

Access ramp at 6 % lengthens from 136.666667 ft to 155.000000 ft to reach the raised berm (C-9 access ramp detail; Attachment A-8).

A separate energy dissipator is detailed at S-15 for the Line B discharge; the spillway apron does not serve it. The HGL Worksheet places S-15 at the basin’s north face while the FM Check Print runs the Line B corridor along the south edge; the drainage lead confirms the entry point before detailing it.

HGL Worksheet rerun under G-5 with the emergency tailwater at 2,859.273284 ft (0.773284 ft above the worksheet’s 2,858.50-ft case) and the S-15 rim at 2,860.30 ft.

Outfall stub invert. C-6 takes the existing 30-in stub invert of 2,850.75 ft “per Phase 2 as-builts,” but the Ph2 As-Builts (RD-1 through RD-5) record no stub at the southwest corner; 2,850.75 ft appears there only as the Roadway A centerline grade at Sta. 10+00. The invert is field-verified before the outlet rating is finalized.

Engineer’s Estimate (10/10/2026). It carries 500 SY of loose riprap, D50 = 12 in (item 2.42), and no articulated block or grouted riprap; Section 2 and embankment (item 1.09) quantities are updated before the bond figure is final.

Disposition 3. The revised C-9 carries the spillway on the south berm with the crest held at 2,858.50 ft, a 50.0-ft crest, an 88.4-cfs design discharge with the outlet blocked, a 2,859.27-ft design water surface, the top of berm at 2,860.30 ft, 1.03 ft of spillway freeboard and 2.39 ft of 100-year freeboard, all dimensioned; full-length armor into a lined overflow channel; outlet works matched to MDS App. D-2; and basin notes that cite the allocation, state the freeboard correctly, define the overflow path and assign maintenance (Attachment B).

6.  Where the Overflow Goes

As drawn, the spillway is on the east berm (C-6; C-9). On the FM Check Print (Sheet 4), the east line of Parcel E abuts residential Lots 51 and 57. C-9 assumes “natural grade beyond the berm at elevation 2,853.00′,” but Phase 3 grading sets the pads of Lots 39 through 60 at 2,862.0 ft to 2,868.0 ft, stepping down toward the basin (C-7) — at least 3.50 ft above the crest. Water leaving the east berm drops into the strip between the berm toe and the rear yards of Lots 51 and 57 and cannot continue east. If Parcel E were a band of uniform width around the 293-ft by 195-ft top-of-berm line (C-6), its 2.04 ac would give 29.049164 ft; the drawn crest and exterior face use 22.50 ft of that, leaving 6.549164 ft beyond the toe before the lot line (Attachment A-8). No swale, channel or easement for the overflow appears on C-6, C-9 or the map; the only drainage easement on the map is 15 ft along the west line of Parcel D (FM Check Print, Sheet 3). The water’s route out is south along and across those rear yards and over the strip Sheet 4 labels “Line B storm drain corridor” — which the map makes neither a lot, nor part of Parcel E, nor an easement — to Windmill Lane. The C-9 note that flow “spreads to downstream open swale in Common-Area Parcel ‘E’ and exits at Windmill Ln. gutter line” describes a facility that is not drawn, and Public Works comment G-6 (Ph3 Comments) already reports gutter spread that appears to exceed the half-street criterion at the Windmill Ln./Desert Sage Pkwy. low point.

Disposition 4 — Today the overflow ends up on private Lots 51 and 57. On the revised C-9 it leaves the south berm into the lined overflow channel inside Parcel E, crosses the Line B corridor strip inside a drainage easement in favor of the Association shown on the resubmitted FM-26-100290 (giving the strip the status its label already implies; no lot line or Parcel E line moves), enters the Windmill Lane gutter through a curb-and-walk outlet in the Phase 3 half-street improvements (TM COA Condition 4) sized for 88.4 cfs, and flows west in Windmill Lane toward Rainbow Boulevard and the regional system at the southwest corner (MDS §2.1; §5.1). The spillway is positioned so the channel meets Windmill Lane where the gutter falls west, downstream of the Desert Sage Pkwy. low point, and the G-4 package shows Windmill Lane carrying the 88.4 cfs plus its own 100-year flow within the right-of-way, checked together with the G-6 inlet redesign. The crossing of the Windmill Lane frontage is kept clear of trees and walk obstructions on Sheet L-2, Section C. No overflow is directed onto any lot.

7.  Actions

| No. | Action | Owner | Due |
| --- | --- | --- | --- |
| 1 | G-4 calculation package; revised C-9 spillway detail, sections and basin notes; C-6 callouts (Sections 5 and 6) | Drainage lead | 11/13/2026 |
| 2 | Outlet works redesigned to the MDS App. D-2 rating; rating table on C-9 | Drainage lead | 11/13/2026 |
| 3 | Fit of the raised embankment inside Parcel E on the plotted base; drainage easement over the Line B corridor strip on FM-26-100290, Sheet 4 | Survey group, with drainage lead | 11/13/2026 |
| 4 | Windmill Lane receiving capacity and overflow entry location, checked with the G-6 inlet redesign | Drainage lead, with Priya Sarwal | 11/13/2026 |
| 5 | HGL Worksheet rerun (tailwater 2,859.273284 ft; S-15 rim 2,860.30 ft; S-15 dissipator) under G-5 | Drainage lead | 11/13/2026 |
| 6 | Clear zone at the overflow crossing on Sheet L-2, Section C | Bea Cortland, PLA | 11/13/2026 |
| 7 | Independent back-check of the revised C-9 against Attachment A by a reviewer who did not draft it; QA/QC Tab 3 items 26 through 29 re-run | Jonathan R. Kessler, PE, with Priya Sarwal | 11/20/2026 |
| 8 | Engineer’s Estimate quantities updated to the revised C-9; revised bond figure to Callaway | Max Braddock | 11/22/2026 |
| 9 | Preliminary detention calculation (09/25/2026) marked superseded, not for use | Max Braddock | 11/02/2026 |
| 10 | Phase 3 supplemental declaration adding Parcel E and its drainage facilities to CC&R Exhibit B (TM COA Condition 16; CC&Rs §3.3) | Callaway Land Partners, with Vogel & Marsh LLP | With the FM-26-100290 recordation package (target 12/18/2026) |

Nothing in the engineering needs a decision from Callaway; the one item on your side is Action 10. If the fit check in Action 3 shows the raised embankment cannot be held inside Parcel E with a longer crest, I will call you the same day, before anything goes to the County. The G-4 calculation package is sealed by the Engineer of Record.

This review is a desk check of the records in Attachment C; it involved no field verification. The Parcel E fit and the Windmill Lane capacity are confirmed under Actions 3 and 4.

______________________________________

Max Braddock

Project Manager, Sundial Engineering & Survey

(702) 555-0144 · mbraddock@sundialensv.com

Attachments:  A — Calculations.  B — Draft text for the revised Sheet C-9 spillway detail and basin notes.  C — Records relied on.

ATTACHMENT A — CALCULATIONS

Conventions: elevations in ft, NAVD 88 (C-1); g = 32.2 ft/s2; intermediate values are carried unrounded and shown to six decimal places; head H is measured above the crest from the basin pool with approach velocity head neglected; adopted sheet values are rounded to 0.01 ft per C-1 General Notes (spot elevations to two decimal places), with the top of berm rounded up.

A-1  Freeboard arithmetic, C-9 as drawn  (inputs: C-6; C-9; MDS App. D-2)

| Quantity | Computation | Result | C-9 states |
| --- | --- | --- | --- |
| Crest above 100-yr WSEL | 2,858.50 ft − 2,857.91 ft | 0.59 ft | 0.71 ft (spillway detail); 0.60 ft (Basin Notes) |
| Top of berm above crest | 2,859.20 ft − 2,858.50 ft | 0.70 ft | 0.70 ft (Basin Notes) |
| Top of berm above 100-yr WSEL | 2,859.20 ft − 2,857.91 ft | 1.29 ft | 1.29 ft (Basin Notes) |
| 100-yr WSEL above basin bottom | 2,857.91 ft − 2,851.00 ft | 6.91 ft | — |

A-2  Capacity of the spillway as drawn

Q = C L H1.5; L = 20.0 ft (C-6; C-9); Hmax = 0.70 ft (A-1); design discharge 88.4 cfs (MDS App. C-2, D-1; Hydrology Worksheet B13).

| Step | Computation | Result |
| --- | --- | --- |
| Hmax1.5 | (0.70 ft)1.5 | 0.585662 ft1.5 |
| Qmax, C = 2.6 ft0.5/s | 2.6 ft0.5/s × 20.0 ft × 0.585662 ft1.5 | 30.454425 cfs = 34.450707 % of 88.4 cfs |
| Theoretical ceiling C | (2/3)1.5 × (32.2 ft/s2)0.5 | 3.088809 ft0.5/s |
| Qmax, C = 3.088809 ft0.5/s | 3.088809 ft0.5/s × 20.0 ft × 0.585662 ft1.5 | 36.179962 cfs = 40.927559 % of 88.4 cfs |
| Head to pass 88.4 cfs, C = 2.6 ft0.5/s | [88.4 cfs / (2.6 ft0.5/s × 20.0 ft)]2/3 = (1.700000 ft1.5)2/3 | 1.424402 ft → WS 2,859.924402 ft, 0.724402 ft above 2,859.20 ft |
| Head to pass 88.4 cfs, C = 3.088809 ft0.5/s | [88.4 cfs / (3.088809 ft0.5/s × 20.0 ft)]2/3 | 1.269855 ft → WS 2,859.769855 ft, 0.569855 ft above 2,859.20 ft |

A-3  Freeboard floor with the crest held at 2,858.50 ft

Required top of berm = crest + H + 1.0 ft ≥ 2,858.50 ft + 0 ft + 1.0 ft = 2,859.50 ft for any crest length. The existing 2,859.20 ft (C-6; C-9) is 0.30 ft short before any head is added.

A-4  Revised spillway: L = 50.0 ft, C = 2.6 ft0.5/s, b = 6.0 ft

| Step | Computation | Result |
| --- | --- | --- |
| Q / (C L) | 88.4 cfs / (2.6 ft0.5/s × 50.0 ft) | 0.680000 ft1.5 |
| Design head H | (0.680000 ft1.5)2/3 | 0.773284 ft |
| H/b | 0.773284 ft / 6.0 ft | 0.128881 (dimensionless) |
| Design water surface | 2,858.50 ft + 0.773284 ft | 2,859.273284 ft |
| Required top of berm | 2,859.273284 ft + 1.0 ft | 2,860.273284 ft → adopted 2,860.30 ft |
| Freeboard provided | 2,860.30 ft − 2,859.273284 ft | 1.026716 ft |
| Berm raise | 2,860.30 ft − 2,859.20 ft | 1.10 ft |
| Freeboard, 100-yr WSEL | 2,860.30 ft − 2,857.91 ft | 2.39 ft |
| Notch top width (4H:1V) | 50.0 ft + 2 × 4 × (2,860.30 ft − 2,858.50 ft) | 64.40 ft |
| Flow top width at design WS | 50.0 ft + 2 × 4 × 0.773284 ft | 56.186276 ft |
| Unit discharge q | 88.4 cfs / 50.0 ft | 1.768 cfs/ft |
| Critical depth on crest | [(1.768 cfs/ft)2 / 32.2 ft/s2]1/3 | 0.459589 ft; velocity 3.846916 ft/s |

Rating, rectangular crest only (notch side slopes not counted):

| Stage (ft) | H (ft) | Q = C L H1.5, C L = 130.0 ft1.5/s (cfs) |
| --- | --- | --- |
| 2,858.50 | 0.000000 | 0.000000 |
| 2,858.75 | 0.250000 | 16.250000 |
| 2,859.00 | 0.500000 | 45.961941 |
| 2,859.273284 | 0.773284 | 88.400000 (design) |
| 2,859.50 | 1.000000 | 130.000000 |
| 2,860.30 (top of berm) | 1.800000 | 313.943944 (3.551402 × design) |

Required top of berm versus crest length (supports the fit rule in Section 5.5; C = 2.6 ft0.5/s, Q = 88.4 cfs):

| Crest length L (ft) | H (ft) | Design WS (ft) | Required top of berm (ft) |
| --- | --- | --- | --- |
| 20.0 (as drawn) | 1.424402 | 2,859.924402 | 2,860.924402 |
| 30.0 | 1.087022 | 2,859.587022 | 2,860.587022 |
| 40.0 | 0.897317 | 2,859.397317 | 2,860.397317 |
| 50.0 (adopted) | 0.773284 | 2,859.273284 | 2,860.273284 → 2,860.30 |
| 60.0 | 0.684781 | 2,859.184781 | 2,860.184781 |
| 80.0 | 0.565274 | 2,859.065274 | 2,860.065274 |
| 100.0 | 0.487139 | 2,858.987139 | 2,859.987139 |
| Limit, L → ∞ | 0.000000 | 2,858.50 | 2,859.50 |

A-5  Apron geometry as drawn  (inputs: C-9 apron and crest; C-6 exterior slope 3H:1V)

| Step | Computation | Result |
| --- | --- | --- |
| Fall, crest to natural grade | 2,858.50 ft − 2,853.00 ft | 5.50 ft |
| Horizontal run at 3H:1V | 3 × 5.50 ft | 16.50 ft |
| Slope length | 5.50 ft × 100.5 | 17.392527 ft |
| Shortfall of 15-ft apron | 16.50 ft − 15.0 ft; 17.392527 ft − 15.0 ft | 1.50 ft horizontal; 2.392527 ft along slope |

A-6  C-9 outlet orifice versus MDS App. D-2

Q = Cd A (2 g h)0.5; Cd = 0.60 (dimensionless, sharp-edged plate, assumed); A = 1.0 ft × 1.5 ft = 1.5 sf; h = stage − 2,851.50 ft (C-9 outlet detail, centroid of opening).

| Stage (ft) | h (ft) | (2gh)0.5 (ft/s) | Q, C-9 orifice (cfs) | Q, App. D-2 (cfs) | Difference |
| --- | --- | --- | --- | --- | --- |
| 2,853.00 | 1.500000 | 9.828530 | 8.845677 | 4.9 | +3.945677 cfs (+80.524019 %) |
| 2,855.00 | 3.500000 | 15.013327 | 13.511995 | 12.6 | +0.911995 cfs (+7.238053 %) |
| 2,857.00 | 5.500000 | 18.820202 | 16.938182 | 23.1 | −6.161818 cfs (−26.674538 %) |
| 2,857.91 | 6.410000 | 20.317579 | 18.285821 | 27.9 | −9.614179 cfs (−34.459424 %) |
| 2,858.50 | 7.000000 | 21.232051 | 19.108846 | 41.5 | −22.391154 cfs (−53.954588 %) |

Cd needed for 27.9 cfs at 2,857.91 ft = 27.9 cfs / (1.5 sf × 20.317579 ft/s) = 0.915463 (dimensionless).

A-7  Storage check (average end area, C-9 contour areas) and preliminary-calculation comparison

| Elevation (ft) | Contour area (sf) | Increment (ac-ft) | Cumulative (ac-ft) | C-9 / MDS App. D-2 (ac-ft) |
| --- | --- | --- | --- | --- |
| 2,851.00 | 29,450 | — | 0.000000 | 0.00 |
| 2,852.00 | 32,380 | 0.709711 | 0.709711 | 0.71 |
| 2,853.00 | 35,420 | 0.778237 | 1.487948 | 1.49 |
| 2,854.00 | 38,600 | 0.849633 | 2.337580 | 2.34 |
| 2,855.00 | 41,910 | 0.924128 | 3.261708 | 3.26 |
| 2,856.00 | 45,340 | 1.001492 | 4.263200 | 4.26 |
| 2,857.00 | 48,900 | 1.081726 | 5.344927 | 5.34 |
| 2,857.91 | 52,250 | 1.056548 | 6.401475 | 6.40 (Table 4-1: 6.4) |
| 2,858.50 | 54,480 | 0.722804 | 7.124279 | 7.12 |
| 2,859.20 | 57,180 | 0.897176 | 8.021455 | 8.02 |

Increment = (A1 + A2) / 2 × Δh / 43,560 sf/ac. Preliminary calc: 8.1 ac-ft − 6.4 ac-ft = 1.7 ac-ft (26.5625 % over the allocation); 8.1 ac-ft − 8.021455 ac-ft = 0.078545 ac-ft over the storage to today’s top of berm.

A-8  Footprint and access ramp

| Step | Computation | Result |
| --- | --- | --- |
| Embankment widening per side | (4 + 3) × 1.10 ft | 7.70 ft (interior top line 4.40 ft; exterior toe a further 3.30 ft) |
| Interior top line at 2,860.30 ft | (293 ft + 8.80 ft) × (195 ft + 8.80 ft), from C-6 293 ft × 195 ft | 301.80 ft × 203.80 ft |
| Current top-of-berm footprint | 293 ft × 195 ft | 57,135 sf = 1.311639 ac (C-6: ≈ 1.31 ac) |
| Parcel E | 2.04 ac × 43,560 sf/ac (FM Check Print, Sheet 4) | 88,862.4 sf; 31,727.4 sf outside the top-of-berm line |
| Illustrative uniform band d | (293 ft + 2d)(195 ft + 2d) = 88,862.4 sf | 29.049164 ft |
| East spillway as drawn | 6.0 ft crest + 16.50 ft face | 22.50 ft; 6.549164 ft left beyond the toe |
| Access ramp at 6 % | (2,859.20 ft − 2,851.00 ft) / 0.06 → (2,860.30 ft − 2,851.00 ft) / 0.06 | 136.666667 ft → 155.000000 ft |

ATTACHMENT B — DRAFT TEXT FOR THE REVISED SHEET C-9

Sheet language for the drainage lead. Values are from Attachment A; sources are the records named in Attachment C.

Detail — Emergency Spillway (Revised)

Broad-crested weir on the south berm of the detention basin, Common-Area Parcel “E.” Crest elevation 2,858.50 ft. Crest length 50.0 ft (along berm). Crest breadth 6.0 ft (direction of flow). Notch side slopes 4H:1V from crest to top of berm 2,860.30 ft; notch top width 64.40 ft.

Design discharge 88.4 cfs: Phase 3 100-year peak inflow, Master Drainage Study — Desert Sage Ranch (140 acres), Revision 1, February 2022, Appendices C-2 and D-1. Outlet works assumed fully blocked and basin at crest when the peak arrives; no credit for storage or outlet discharge.

Q = C L H1.5, C = 2.6 ft0.5/s. Design head 0.77 ft. Spillway design water surface 2,859.27 ft.

Freeboard 1.03 ft from spillway design water surface (2,859.27 ft) to top of berm (2,860.30 ft); minimum 1.0 ft. Crest 0.59 ft above the 100-year water surface (2,857.91 ft).

Crest surface: articulated concrete block over geotextile filter fabric.

Exterior face (3H:1V) and apron: grouted riprap, D50 = 12 in, on bedding and geotextile; layer thickness, bedding gradation, toe-down depth and stone size as dimensioned on the spillway section per the CCRFCD Hydrologic Criteria and Drainage Design Manual calculation at unit discharge 1.768 cfs/ft. Armor continuous across the full 64.40-ft notch, down the full exterior face past the toe, and through the overflow channel to the Windmill Lane right-of-way; edges keyed; cutoff at downstream end.

Overflow channel: lined channel within Common-Area Parcel “E” and the drainage easement shown on FM-26-100290, discharging to the Windmill Lane gutter through a curb-and-walk outlet sized for 88.4 cfs per the Clark County Uniform Standard Drawings, located where the Windmill Lane gutter falls west, downstream of the Desert Sage Pkwy. low point.

No fence, gate, wall, tree or structure across the spillway crest or the overflow channel.

Spillway rating (rectangular crest only): 2,858.50 ft — 0 cfs; 2,858.75 ft — 16.25 cfs; 2,859.00 ft — 45.96 cfs; 2,859.27 ft — 88.4 cfs (design); 2,859.50 ft — 130.00 cfs; 2,860.30 ft (top of berm) — 313.94 cfs.

Vertical dimension string: basin bottom 2,851.00 ft | 6.91 ft | 100-year WSEL 2,857.91 ft | 0.59 ft | crest 2,858.50 ft | 0.77 ft | spillway design water surface 2,859.27 ft | 1.03 ft | top of berm 2,860.30 ft.

Basin Notes (Revised)

1.  The detention basin provides the Phase 3 detention allocation of 6.4 acre-feet established in Table 4-1 of the Master Drainage Study — Desert Sage Ranch (140 acres), Sundial Engineering & Survey, Revision 1 dated February 2022, accepted by the Clark County Regional Flood Control District by letter dated 02/28/2022. Storage provided between the basin bottom (2,851.00 ft) and the 100-year water surface (2,857.91 ft) is 6.40 acre-feet (Storage Summary Table, this sheet).

2.  The outlet works reproduce the stage–discharge relationship of Master Drainage Study Appendix D-2: 4.9 cfs at 2,853.00 ft; 12.6 cfs at 2,855.00 ft; 23.1 cfs at 2,857.00 ft; 27.9 cfs at 2,857.91 ft; 41.5 cfs at 2,858.50 ft. Shared-outfall discharge for the fully developed 140-acre site remains at or below Q100 = 78 cfs.

3.  Freeboard with the outlet works operating: 100-year water surface 2,857.91 ft to top of berm 2,860.30 ft = 2.39 ft (minimum 1.0 ft).

4.  Emergency spillway (see Detail): south berm; crest 2,858.50 ft, 0.59 ft above the 100-year water surface; crest length 50.0 ft; design discharge 88.4 cfs with the outlet works fully blocked; spillway design water surface 2,859.27 ft; freeboard to top of berm 1.03 ft (minimum 1.0 ft).

5.  Minimum rim elevation 2,860.30 ft around the entire basin perimeter except at the spillway crest, provided by compacted embankment or by adjoining finished grade. All embankment, spillway, armor and overflow channel lie within Common-Area Parcel “E” or the drainage easement shown on FM-26-100290.

6.  Spillway discharge is carried south in the lined overflow channel to the Windmill Lane right-of-way and flows west in Windmill Lane toward Rainbow Boulevard. No spillway or overflow discharge is directed onto any lot.

7.  Common-Area Parcel “E” and all basin appurtenances — outlet works, emergency spillway, armor, overflow channel, access ramp, gate and maintenance path — are owned and maintained by the Desert Sage Ranch Community Association. Parcel “E” and these improvements are added to Exhibit B (Common Area Maintenance Exhibit) of the Declaration of CC&Rs, Instrument No. 20241223-0004422, by the Phase 3 supplemental declaration recorded with FM-26-100290. The Association inspects the spillway, armor and overflow channel after any event in which the water surface reaches the spillway crest (2,858.50 ft) and restores them in accordance with the approved operations and maintenance manual.

8.  Basin bottom shall be graded to drain to the outlet control structure at a minimum longitudinal slope of 0.5 %. No standing water within 72 hours of a design event.

Delete from the current sheet

Spillway detail callout “(0.71′ above 100-year water surface).”

Spillway detail callout “flow spreads to downstream open swale in Common-Area Parcel ‘E’ and exits at Windmill Ln. gutter line.”

Apron dimension “15′ × 20′.”

Basin Note “Freeboard between the 100-year water surface (2,857.91′) and the top of berm (2,859.20′) is 1.29′ …”

Basin Note “Emergency spillway crest set at 2,858.50′, 0.60′ above the 100-year water surface and 0.70′ below the top of berm.”

ATTACHMENT C — RECORDS RELIED ON

| Short name | Record | Project file location |
| --- | --- | --- |
| C-1, C-6, C-7, C-9 | Desert Sage Ranch Phase 3 Improvement Plans, Sheets C-1 through C-9, first submittal 08/21/2026 | Design-Drafting/Phase 3/DSR_Ph3_Improvement_Plans_C1-C9.pdf |
| QA/QC Checklist | Phase 3 Plan Set QA/QC Checklist, 08/18/2026 | Design-Drafting/Phase 3/DSR_Ph3_QAQC_Checklist.xlsx |
| MDS | Master Drainage Study — Desert Sage Ranch (140 acres), Revision 1, February 2022 | Reports-Studies/DSR_Master_Drainage_Study.pdf |
| Hydrology Worksheet | Phase 3 Hydrology Worksheet, 07/2026 | Reports-Studies/DSR_Ph3_Hydrology_Worksheet.xlsx |
| HGL Worksheet | Phase 3 Storm Drain HGL Worksheet, 07/2026 | Reports-Studies/DSR_Ph3_StormDrain_HGL.xlsx |
| Preliminary calc | Preliminary Detention Calculation, 09/25/2026 | Reports-Studies/DSR_Ph3_Detention_Calc_prelim.xlsx |
| Ph2 Comments | Clark County Public Works Phase 2 plan check letters, 09/28/2022 and 12/14/2022 | Correspondence/Agency/CC-PW_Ph2_Comments_1st_2nd.pdf |
| Ph2 Response Matrix | Phase 2 Comment Response Matrix, 11/07/2022 | Correspondence/Agency/DSR_Ph2_Comment_Response_Matrix.xlsx |
| FCD Acceptance Letter | CCRFCD acceptance of the MDS, 02/28/2022 | Correspondence/Agency/FCD_MDS_Acceptance_Letter.pdf |
| Ph3 Comments | Clark County Public Works Phase 3 first-round comments, 10/09/2026 | Correspondence/Agency/CC-PW_1stReview_Comments_10092026.pdf |
| FM Check Print | FM-26-100290 plan check submittal, 08/21/2026 | Design-Drafting/Survey/DSR_Ph3_FinalMap_FM-26-100290_checkprint.pdf |
| TM COA | TM-22-500041 Conditions of Approval, 03/14/2022 | Correspondence/Agency/TM-22-500041_Conditions_of_Approval_03142022.pdf |
| CC&Rs | Declaration of CC&Rs with Common Area Maintenance Exhibit, Instr. No. 20241223-0004422 | Tenders-Contracts/DSR_CCRs_CommonArea_Exhibit.pdf |
| L-2 | Phase 3 Landscape Sheets L-1 through L-4 (Sheet L-2, Section C) | Design-Drafting/Landscape/DSR_Ph3_Landscape_L1-L4.pdf |
| Pre-App Notes | Pre-Application Meeting Notes, 06/22/2026 | Meeting Notes/DSR_Ph3_PreApp_Meeting_Notes.docx |
| Engineer’s Estimate | Engineer’s Estimate of Probable Cost, 10/10/2026 | Cost Estimates/DSR_Ph3_Engineers_Estimate.xlsx |
| Ph2 As-Builts | Phase 2 Record Drawings RD-1 through RD-5, 02/2025 | Design-Drafting/Phase 2 As-Builts/DSR_Ph2_AsBuilts.pdf |
| Tracker; coordination e-mail | Resubmittal Tracker (10/31/2026); internal coordination e-mail (10/09/2026) | Correspondence/DSR_Ph3_Resubmittal_Tracker.xlsx; Correspondence/DSR_Ph3_internal_design_coordination.eml |

Phase 2 comment G-4 concerned cross-lot drainage on Lots 22 through 31 and does not bear on this item; the Phase 2 counterparts to Phase 3 G-4 are G-2 (outlet detail reconciled to the study) and G-3 (freeboard of at least 1.0 ft above the design HGL, dimensioned).