THELBRIDGE PROJECT MANAGEMENT SERVICES

500 South High Street, Suite 720, Columbus, OH 43215  |  (614) 555-0125  |  thelbridgepm.com

VERIFICATION MEMORANDUM

To:	Rachel Marlbeck, University Program Director — Thornbury State University, Office of Capital Programs

From:	Adrian Vance, Project Engineer (Structural/Geotechnical), Owner’s Representative — Thelbridge Project Management Services

Date:	07/20/2026

Subject:	Register Item 048 — Block B plant-room support of excavation, Submittal 31-SH-B Rev.1 as supplemented by Rev.2 (Kesterline letter KE-L-2026-0713): verification against logged groundwater and subsurface conditions — NOT VERIFIED

1.  PURPOSE

This memorandum addresses Register Item 048 (Geotechnical — Design): “Verify the Block B plant-room shoring design … against logged site groundwater and subsurface conditions for Package A”, raised by R. Nimkar on 07/10/2026 and required by 07/20/2026. The item was raised against Kesterline Engineering’s Submittal 31-SH-B Rev.1, sealed 06/11/2026. On 07/13/2026 Kesterline issued a sealed Revision 2 Engineering Supplement (letter KE-L-2026-0713) and asked for verification of 31-SH-B “on the basis of Rev.1 as supplemented by Rev.2, so that excavation can proceed on the Contractor’s planned date” of 08/10/2026. I have taken the item over from R. Nimkar and reviewed it on that current revision.

The determinations made are: (a) whether the current revision is consistent with the logged groundwater and subsurface conditions and satisfies the project design basis; (b) which of its checks can be carried forward and which cannot; (c) what the excavation it would release would do to the permanent work already built at Block B; (d) what must be produced, and by whom, before the excavation may start; (e) what the result means for the 08/10/2026 start; and (f) the register response and status. This memorandum also serves as the Thelbridge review comments on the shoring package called for by action item AI-26-06 (Progress Meeting No. 26).

Result: NOT VERIFIED. Item 048 remains Open. The Block B plant-room excavation planned for 08/10/2026 is not released.

2.  DOCUMENTS REVIEWED

Documents relied on are listed below with the short tag used for citations in Sections 3 to 5. Page references are to the page numbers printed on each document; drawings are cited by sheet.

| Tag | Document | Date |
| --- | --- | --- |
| R2 | Kesterline Engineering, PC — Submittal 31-SH-B Rev.2 Engineering Supplement, Block B Plant-Room Support of Excavation, letter KE-L-2026-0713 (B. A. Halvard, PE), 5 pp. | 07/13/2026 (sealed) |
| R1 | Kesterline Engineering, PC — Submittal 31-SH-B Rev.1, Support of Excavation Design Calculations, Block B Plant-Room Excavation, 21 pp. | 06/11/2026 (sealed); Rev.0 07/29/2025 |
| GIR | Kelbrook Geotechnical, Inc. — Geotechnical Investigation Report KGI-2024-0417 Rev.2 | 02/14/2025 |
| BL | Kelbrook Geotechnical — Appendix A, Boring Logs B-01 to B-09 and Groundwater Monitoring Record (19 rounds, 11/22/2024 – 06/28/2026) | 06/30/2026 |
| FOR | Kelbrook Geotechnical — Field Observation Report KGI-FO-2026-0528, Excavation and Groundwater | 05/28/2026 |
| CON | Vantree Materials Testing — Laboratory Consolidation Test Report VMT-2025-0109-CON (ASTM D2435) | 01/09/2025 |
| IDX | Vantree Materials Testing — Geotechnical Laboratory Index Test Data VMT-2024-0917-PkgA-INDEX | 01/09/2025 |
| PRO | Vantree Materials Testing — Modified Proctor Report VMT-25-0918-P04, Package A Structural Fill (Larchwood Pit) | 09/18/2025 |
| DBM | Calloway Braddock — Design Basis Memorandum CB-DBM-001 Rev.2 | 11/14/2025 |
| S-101 | Calloway Braddock — Sheet S-101 Foundation Plan, Rev.4 | 05/29/2026 |
| S-102 | Calloway Braddock — Sheet S-102 Basement Floor Levels, Drainage Zones and Wall-to-Mat Joint Layout, Rev.2 | 12/12/2025 |
| S-201 | Calloway Braddock — Sheet S-201 Foundation Sections and Details, Rev.4 | 05/29/2026 |
| STR-011 | Calloway Braddock — Calculation CB-STR-011, Basement Mat Design, Rev.0 | 12/05/2025 (sealed) |
| GEO-004 | Calloway Braddock — Calculation CB-GEO-004, Block B Driven Pile Design — Capacity | 08/22/2025 (sealed) |
| SPEC | Specification Section 31 20 00, Earth Moving, Rev.3 | 03/06/2026 |
| DW-A | Rowan Bay Constructors — Submittal 31-DW-A Rev.1, Dewatering and Groundwater Control Plan, Block A Basement (sealed B. A. Halvard, PE; EOR stamp 06/12/2025) | 06/04/2025 |
| PIR | Rowan Bay Constructors — Pile Installation Records, Block B, RBC-BB-PIR-2025 | 11/06 – 11/21/2025 |
| FPR | Rowan Bay Constructors — Fill Placement and Grading Records, Block B, RB-FPR-BB-2025 | 10/06 – 11/02/2025 |
| DFR | Rowan Bay Constructors — Daily Field Reports Nos. 141–145, Basement Level | 06/28 – 07/02/2026 |
| VR | Thelbridge — Review Comment and Verification Register, Package A (COVER, REGISTER and SCHEDULE sheets) | updated 07/15/2026 |
| SR | Thelbridge — Submittal Register, Package A | updated 07/13/2026 |
| RFI | Thelbridge — RFI Log, Package A (RFI 048 and RFI 058, raised by Kesterline) | updated 07/13/2026 |
| MIN26 | Thelbridge — Progress Meeting Minutes No. 26 | 07/09/2026 (issued 07/10/2026) |
| MPR14 | Thelbridge — Monthly Progress Report No. 14, June 2026 | 07/06/2026 |
| OD | Thornbury State University — R. Marlbeck e-mail, “Written Verification Required Before Permanent Work” | 07/06/2026 |
| DIR | Thelbridge — Project Directory and Distribution List, Rev.4 | 06/30/2026 |

Specification Sections 31 50 00 (Excavation Support and Protection) and 31 23 19 (Dewatering), to which R1 and DW-A refer, were not in the file available for this review. The determination below does not depend on them.

3.  BASIS OF REVIEW

3.1  Object and nature of the review

The object of review is the current revision as Kesterline asks it to be read: R1 as modified by R2, with R2’s Supersession Statement (R2 p.1) applied literally. Thelbridge verifies the delegated design against the project record. It does not design, and design responsibility remains with Kesterline (R1 §1.5, pp.3–4) and, for the permanent structure, with the EOR. Dispositions follow the register convention: VERIFIED, VERIFIED WITH COMMENT or NOT VERIFIED (VR, COVER). Under the Owner’s directive, no permanent work proceeds until Thelbridge has issued a written verification (OD). The plant-room excavation start is conditioned on closure of Items 048 and 049 and the groundwater component of Item 056 (VR, SCHEDULE item 4; MIN26 item 26.5.2).

3.2  Governing requirements

(a)	GIR, the controlling document for all soil parameters (DBM §9, p.9):

- Table 6-1, stratigraphy and unit weights (p.12).

- §6.3, CL clay su = 900 to 1,100 psf from field vane and UU triaxial tests (p.13).

- §7.1, design water table El. 742.0, to be used for temporary sheeting and dewatering design (p.13).

- §7.2, confined piezometric head El. 738.0 (p.13).

- §8.2, a rigorous base-heave analysis with an appropriate factor of safety; sheeting that extends into the clay must be designed for the differential head across it (pp.15–16).

- §9.4, the dewatering plan and the shoring design must together demonstrate an adequate factor of safety against base heave throughout the excavation, using El. 738.0 (p.18).

- §9.6, every penetration of the clay must be sealed at the aquitard (p.19).

(b)	DBM §6.2 (p.6): a permanent load resisting uplift is taken at 0.9D with an explicit factor of safety, minimum 1.5 for sliding and base heave. DBM §3 site parameters (p.2).

(c)	SPEC: Art. 1.1.B.2 places delegated shoring design under Section 31 50 00 (p.1). Art. 3.6 limits settlement of the completed foundation system to 1.0 in total and 0.5 in differential over 30 ft. Where predicted or monitored settlement exceeds these limits, the EOR is to be notified and no additional load applied until a written disposition is issued (p.5).

(d)	DW-A §1.2 (p.3) and §4.1–4.2 (p.7): the Block A plan does not extend to Block B. Any excavation below about El. 730.0, or approaching the confined aquifer, requires a separately sealed dewatering and groundwater control analysis. DW-A may not be relied on for Block B shoring or for any calculation that treats the excavation as dry or relieved.

(e)	Where the project documents are silent, the designer’s own criteria: FS 1.5 on toe moment and on bending (R2.4, R2.6), H/200 deflection (R1 §12.3, p.18) and the R1 §13.2 action levels (p.19).

3.3  Logged conditions applied

- Shallow water table El. 742.0 (all readings El. 741.6–742.4) and confined head El. 738.0 (all readings El. 737.7–738.3) over 19 rounds to 06/28/2026; the deep piezometers did not respond to fill placement, pile driving or Block A dewatering (BL Table 4-1, pp.13–14; FOR §3.3 p.3, §4.3 and §5.2 p.4).

- Clay from about El. 738.0 to El. 720.0 in both borings inside the pit footprint, with artesian rise to El. 738.0–738.2 on entering the SW-GW and SPT refusal (N ≥ 50 per 6 in) in it (BL: B-04 p.7, B-06 p.9).

- Clay Cc 0.28, e0 0.92, σ′0 1,850 psf, σ′p 1,900 psf (GIR Table 5-1, p.11).

- cv ≈ 4–5 × 10−4 cm²/s in the virgin range and 3.2–3.8 × 10−3 cm²/s in the recompression range (CON, sheets B-06 U3 and B-08 U2).

3.4  Method

For each check I (1) reproduced the arithmetic; (2) tested the inputs against the logged conditions, the GIR and the DBM; (3) tested the assumptions (drainage condition, geometry, loss-of-pumping case) against the record; (4) tested the composite document for internal consistency; and (5) tested the design against the permanent work shown in the record. The calculations in Section 4 are check calculations, not a redesign.

4.  FINDINGS

4.1  Groundwater and stratigraphy inputs agree with the logged record

R2 withdraws the R1 dry-excavation assumption and adopts: the design water table El. 742.0 behind the wall; the clay aquitard from El. 738.0 to El. 720.0, leaving a 6.0-ft plug below subgrade El. 726.0; the aquifer top at El. 720.0; and an unpumped confined head of El. 738.0. These agree with the GIR, with borings B-04 and B-06 inside the pit footprint (base of clay El. 720.0; artesian rise to El. 738.2 and El. 738.0) and with all 19 monitoring rounds through 06/28/2026. Withdrawing the dry assumption was necessary, since DW-A never covered Block B. Unit weights of 120 pcf (CL) and 130 pcf (SW-GW) agree with GIR Table 6-1 and the Vantree index data. The highest confined head recorded is El. 738.3 (P-08, rounds 7 and 18); loss-of-pumping checks should use it.

Record: R2 p.1 (R2.1); GIR pp.12–13 (Table 6-1, §7.1–7.2); BL pp.7, 9, 13; FOR pp.3–4; IDX SUMMARY sheet; DW-A p.3 (§1.2).

4.2  Loading above subgrade (R2.3): arithmetic reproduced, but the fill unit weight is understated

Recomputed with R2’s inputs: σ′v at El. 726.0 = 2,107.6 psf; soil plus surcharge resultant 11,622 lb/ft; water ½ × 62.4 × 16.0² = 7,987 lb/ft acting at El. 731.3; total 19,609 lb/ft; driving moment about the anchor at El. 745.5 = 237,275 ft-lb/ft, against R2’s 237,293; σv0 at subgrade 3,106 psf. The method (layered effective stress plus full hydrostatic pressure from El. 742.0) is appropriate.

R2 carries 118 pcf for the 12 ft of engineered fill, which is the GIR value for the natural SP-SM upper sand. The fill actually placed at Block B is Larchwood Pit SM/SW-SM structural fill. It was compacted to at least 95% of a modified Proctor maximum of 128.4 pcf at −1% to +2% of the 9.2% optimum, so its dry unit weight is at least 122.0 pcf. That gives a moist unit weight of 132.0–135.6 pcf, and about 138.9 pcf saturated (Gs 2.68). On those values the soil load above subgrade rises 10.7%, the total load 6.3%, the driving moment 5.7% (to 250,812 ft-lb/ft) and σv0 by 195 psf (to 3,301 psf).

Record: R2 p.3 (R2.3); R1 p.6 (§3.2); GIR p.12 (Table 6-1); FPR (Cover; Note 3); PRO pp.1–2; SPEC p.4 (Art. 3.4.B).

4.3  Toe embedment (R2.4) rests on a shear strength that the record does not support

R2.4 takes su = 1,400 psf “carried from Rev.1 Section 3.2”. R1 §3.2 attributes that value to “the Geotechnical Report, Section 6 and Table 6.2”, but the GIR has no Table 6.2. It reports su = 900 to 1,100 psf from field vane and UU triaxial tests (§6.3), and the DBM directs that any conflict over soil parameters be resolved in favour of the GIR. The table below applies R2’s own method (net passive pn = 4su − σv0 over D = 6.5 ft, free-earth moments about El. 745.5) and R2’s own loads:

| su (psf) | pn = 4su − σv0 (psf) | Pp over D = 6.5 ft (lb/ft) | MR about El. 745.5 (ft-lb/ft) | FS (1.50 required) |
| --- | --- | --- | --- | --- |
| 1,400 (R2) | 2,494 | 16,211 | 368,800 | 1.55 |
| 1,100 (GIR upper bound) | 1,294 | 8,411 | 191,350 | 0.81 |
| 1,000 | 894 | 5,811 | 132,200 | 0.56 |
| 900 (GIR lower bound) | 494 | 3,211 | 73,050 | 0.31 |

The check reaches 1.50 only if su ≥ 1,378 psf, which is above the top of the logged range. It also fails on R2’s own su in two other cases:

- With the as-placed fill unit weight (Finding 4.2), FS = 1.36.

- If the sheets stop at the top of the SW-GW (El. 720.0, D = 6.0 ft), FS = 1.42.

The second case is a real possibility. The revised tip requires driving 0.5 ft into SW-GW logged at SPT refusal (N ≥ 50 blows per 6 in). The only driveability statement that remains in force is R1 §11.3, which covers a 28-ft sheet tipped at El. 722.0 in CL clay at about 30 blows/ft. R2 also applies the clay strength to the 0.5 ft of embedment in sand and gravel.

Record: R2 p.3 (R2.4); R1 p.6 (§3.2), p.16 (§11.3); GIR p.9 (§3.2), p.13 (§6.3, §6.4); DBM p.9 (§9); BL pp.7, 9.

4.4  The undrained condition cannot be relied on for the exposure period; drained, the clay gives no net toe resistance

R2.4 justifies an undrained check by the permeability of the clay (~10−8 cm/s). How long the undrained condition lasts depends on the coefficient of consolidation and the drainage path, not on permeability alone. The passive zone is the 6.0-ft plug inside the pit. It drains at the top to the sumps that keep the pit dry at El. 726.0 (R2.1) and at the bottom to the depressurised aquifer, so the drainage path is 3.0 ft. With the Vantree coefficients, 90% dissipation of the excavation-induced pore pressures takes about 23 days (recompression-range cv ≈ 0.33 ft²/day, which applies to the unloaded plug) to about 187 days (virgin-range cv ≈ 0.04 ft²/day). For comparison, the works are planned to last 4 to 6 months (R1 §4.4, §6.1), with pumping until the plant-room slab is cast (R2.1). R1 itself adopted drained parameters as governing for that duration (§6.1).

I also computed the drained case, using R1’s own drained clay parameters (φ′ = 26°, c′ = 100 psf; these do not appear in the GIR either) and R2.3’s water regime. The net resisting pressure below subgrade (passive minus active minus net water pressure, with cohesion credited on both faces) is negative over the entire embedment:

- Hydrostatic water (El. 742.0 behind the wall, El. 726.0 in front): −1,375 psf at El. 726.0 to −626 psf at El. 720.0.

- Steady seepage to the pumped aquifer head of El. 726.5: −982 psf to −84 psf.

In the drained state, therefore, the clay above El. 720.0 provides no toe resistance at any embedment. The design also does not address the differential head across sheeting that extends into the clay (GIR §8.2, item 3). No toe embedment within the clay can be made to work, and the support system has to be re-engineered.

Record: R2 p.2 (R2.1), p.3 (R2.4); R1 p.6 (§3.2), p.7 (§4.4), p.10 (§6.1); CON (B-06 U3, B-08 U2 and Summary sheets); GIR p.16 (§8.2 item 3).

4.5  Tieback anchors (R2.5): the bond zone lies in the clay, and the capacity is below the design load

The anchors start at El. 745.5 and are inclined 20° below horizontal, with a 25-ft free length and a 24-ft bond length. The bond zone therefore runs from El. 745.5 − 25 sin 20° = El. 737.0 to El. 745.5 − 49 sin 20° = El. 728.7. That is entirely within the CL clay (El. 738.0–720.0), and it extends about 46 ft horizontally behind the wall. R1 §10.1 describes the bond as “seated in the deep sand and gravel stratum below El. 720.0”; at 20° that would need an axial length of 74.6 ft.

The adopted bond stress of 20 psi (2,880 psf) is, by R1 §10.4’s own citation, a pressure-grouted dense sand-and-gravel value. It is 2.6–3.2 times the logged su of the clay in which the bond actually sits, and grout-to-ground shear cannot exceed the shear strength of that clay. On R2.5’s 6.0-in hole the ultimate capacity is therefore at most π × 0.5 ft × 24 ft × su = 33.9–41.5 kips (α = 1.0). That is 0.60–0.74 of the 56.2-kip design load and 0.45–0.55 of the 74.8-kip proof load. The anchors as detailed would fail proof testing after the sheets are driven and the first lift is taken. R2 nevertheless makes that proof test “the demonstration of anchor performance”.

Three further points:

- R2.5 provides for casing “grouted over the aquitard interval to seal against artesian seepage”. That does not match the anchor geometry, since the anchors never reach the aquifer.

- The anchor reaction credits the allowable passive force (16,211 / 1.5 = 10,807 lb/ft) in horizontal equilibrium. The passive force needed for moment equilibrium is 237,293 / 22.75 = 10,430 lb/ft, which gives Th = 9,180 lb/ft (58.6 kips per anchor, 4% above R2.5).

- R2.5 draws its tendon and bond stress from R1 §10.1 and §10.4, which R2’s own Table 1 declares superseded.

Record: R2 p.1 (Table 1), pp.3–4 (R2.5); R1 p.15 (§10.1, §10.4); GIR p.13 (§6.3).

4.6  Base heave and depressurisation (R2.1, R2.2, R2.7 trigger): the arithmetic is right, but the controls and the failure case do not meet DBM §6.2 or GIR §9.4

Reproduced: plug weight W = 6.0 × 120 = 720 psf; 0.9W = 648 psf. At the controlled head of El. 726.5 the uplift is u = 6.5 × 62.4 = 405.6 psf, so FS = 0.9W/u = 1.60. The controls built around that number do not hold:

- Stop-work trigger. R2.7 lets excavation continue until a piezometer exceeds El. 727.0. At El. 727.0 the uplift is 436.8 psf and 0.9W/u = 1.48, below the 1.5 minimum. The highest head compatible with DBM §6.2 at subgrade is El. 726.9, before any allowance for instrument accuracy or response time.

- Loss of pumping. At the logged head of El. 738.0 the uplift at subgrade is 1,123.2 psf. Then 0.9W/u = 0.58 (0.57 at El. 738.3), and even unfactored the plug weighs only 0.64 of the uplift. Crediting full shear on the plug perimeter at the logged su (GIR §8.2; R1 plan 68 × 44 ft) raises the factored ratio only to about 0.94–1.02.

- Hold elevation. With no pumping, the factor falls below 1.5 once the excavation passes El. 735.6 and reaches 1.0 at El. 730.4. R2 requires the 72-hour confirmation only before excavating below El. 732.0, where the unpumped factor is 1.15, and its piezometer trigger applies only below El. 732.0.

- Undesigned system. From El. 735.6 down, stability rests entirely on four pumped wells, and R2 does not design them. It provides no pumping test, no aquifer transmissivity or storage, and no well-yield or drawdown calculation for an aquifer that is at least 60 ft thick, very dense and recharged upgradient. It has no standby pumps, power or alarms, no procedure for loss of pumping (for example, controlled re-flooding of the pit), and no discharge estimate or permit. GIR §9.4 requires the dewatering plan and the shoring design together to demonstrate the factor of safety, and DW-A requires a separately sealed groundwater control analysis for this condition. The Submittal Register records Block B groundwater control as “addressed by shoring cutoff (31-SH-B)”, yet R2.4 states that the sheets are “not credited as a cutoff”. No Block B dewatering submittal exists, and the Block B dewatering change-order proposal CO-19 is still in negotiation.

- Termination. Pumping is to stop when the plant-room slab is cast (R2.1). That criterion is not tied to the permanent structure’s ability to resist the El. 738.0 confined uplift, which is for the EOR to set.

Record: R2 p.2 (R2.1), p.3 (R2.2), p.4 (R2.7); DBM p.6 (§6.2); GIR p.13 (§6.4, §7.2), pp.15–16 (§8.2), p.18 (§9.4); BL p.13; DW-A p.3 (§1.2), p.7 (§4.1); SR (31-DW-A, 31-SH-B entries); MPR14 p.6 (§7).

4.7  Remaining checks

- R2.6, bending. Reproduced: zero shear at El. 733.1 and Mmax = 62.5 kip-ft/ft (R2: 62.4), against Mallow = 30 ksi × 48.5 in³/ft ÷ 12 = 121 kip-ft/ft. The section capacity stands. The demand does not, because it depends on the support conditions in 4.3–4.5; with the equilibrium-consistent anchor reaction alone it rises to 67.2 kip-ft/ft.

- R2.7, deflection. The 1.3-in prediction (against H/200 = 1.44 in) depends on the same failed support conditions. It also exceeds the 1.20-in “stop excavation” action level of R1 §13.2, which R2 keeps in force, so the design predicts that its own stop-work level will be reached. And H/200 is a generic limit that is not related to the permanent work beside the pit (Finding 4.9).

- R1 §8, sliding and overturning (kept in force). These checks (FS 2.06) use the dry-case forces PA = 17,844 lb/ft and T = 15,354 lb/ft, which no longer exist.

- R1 §11.3, driveability (kept in force). This covers 28-ft sheets to El. 722.0 in clay, not 30.5-ft sheets into SW-GW at refusal.

- R1 §11.4, wale (kept in force). Doubled MC12×50 spanning 6 ft between anchors: demand 70.7 kip-ft at 15,700 lb/ft against an allowable 223 kip-ft. That capacity statement stands, provided the re-derived anchor reaction does not exceed 15,700 lb/ft.

Record: R2 p.4 (R2.6, R2.7); R1 p.13 (§8), pp.16–17 (§11.2–11.4), p.18 (§12), p.19 (§13.2).

4.8  “Rev.1 as supplemented by Rev.2” is not a coherent document

R2’s supersession matrix gives R1 section numbers titles that do not match R1’s contents. As a result it keeps in force provisions that R2 itself withdraws, and it supersedes sections whose substance it then relies on:

| Rev.1 § | Title and status given in R2 Table 1 | What R1 actually contains (page) |
| --- | --- | --- |
| 1, 2 | “Project Scope, Codes & Site Reference Documents” — in force | §1.3: toe El. 722.0, D = 4 ft, “toed entirely within cohesive stratigraphy”; §2: design “assumes a dry excavation … per [31-DW-A]” (pp.3, 5) |
| 3.3, 4.2 | Soil parameters; surcharge and equipment loads — in force | Blended profile, Ka = 0.333; surcharge pressure 83 psf on that Ka (pp.6–7). Conflicts with R2.3’s layered analysis. |
| 4.3 | “Lateral Earth Pressure Diagram Above Subgrade” — superseded | Water-bearing load: none, because the excavation was assumed dry (p.7) |
| 5 | “Excavation Base Stability Verification” — superseded | Active earth pressure, blended 950 psf. R1 has no base-stability section (pp.8–9). |
| 6 | “Sheet-Pile Toe Embedment Analysis” — superseded | Passive earth pressure (p.10) |
| 7 | “Tieback Ground Anchor Design” — superseded | Global stability: force and moment equilibrium (pp.11–12) |
| 8 | “Global Overturning & Sliding” — in force | Sliding and overturning, computed with the §7 dry-case forces (p.13) |
| 9 | “Sheet-Pile Structural Bending & Shear” — superseded | Toe embedment check (p.14) |
| 10 | “Wall Deflection & Instrumentation Triggers” — superseded | Tieback anchor design (p.15). R2.5 still cites §10.1 and §10.4. |
| 11.1–11.2 | Not listed | Bending check under dry loads (pp.16–17) |
| 11.3, 11.4 | “Waler, Bearing Plate & Anchor Head Details” — in force | §11.3: driveability of a 28-ft sheet to El. 722.0 in CL; §11.4: wale (pp.16–17) |
| 12, 13 | “Construction Sequence Notes & Submittal Drawings” — in force | §12: deflection 1.2 in; §13: 31-DW-A dewatering started 14 days ahead, tip El. 722.0, lock-off 75 kips, sheet extraction, piezometers “per Submittal 31-DW-A”, stop excavation at 1.20 in (pp.18–19) |
| 14 | Not listed | Conclusion. §14.3: the result depends on a dry excavation per 31-DW-A and a tip at El. 722.0 (p.20). |

In consequence, the following all remain in force:

- the dry-excavation basis (R1 §2; §13.1 step 2; §13.2 piezometers “per Submittal 31-DW-A”);

- the El. 722.0 toe, “entirely within cohesive stratigraphy” (§1.3, §11.3);

- a 75-kip lock-off (§13.1 step 5), against R2’s 42.2 kips;

- a 1.2-in deflection estimate (§12.2), against R2’s 1.3 in.

R1 §11.1–11.2 and §14 are neither kept nor superseded; §14.3 states that the result depends on a dry excavation and a tip at El. 722.0. Two process points: R2 claims conformance with Section 31 20 00 “Earthwork and Support of Excavation”, but 31 20 00 is Earth Moving and refers delegated shoring to Section 31 50 00. And R2 was issued by letter to Thelbridge and the Contractor rather than transmitted by the Contractor; it does not appear on the Submittal Register, where 31-SH-B ends at Rev.1 “Under review”.

Record: R2 p.1 (Supersession Statement, Table 1), p.3 (R2.4 amendment of R1 §13.1 item 3), p.4 (R2.5, R2.7); R1 pp.3–20; SPEC p.1 (Art. 1.1.B.2); SR (31-SH-B entries).

4.9  The design does not recognise the permanent work at the excavation location

Five things in the record bear on where the pit is:

- S-101 Rev.4 (issued 05/29/2026, before R1 was sealed, and cited by R1 §1.3 for the pit geometry) outlines the plant-room excavation at grids H–L / 3–5. That is inside the Blocks A/B basement mat (grids B–L / 1–5, cast 01/12/2026). Its note says the excavation is “to be performed under a separate work package following completion of the mat above”. The southernmost (eighth) row of six Block B piles is plotted on the north line of the outline, at grid H.

- S-102 Rev.2 shows grids H–L as basement Zone 2: mat top El. 734.5, drain K-6 and wall-to-mat joint CJ K-5, whose waterproofing was inspected on 04/09/2026 (VR Item 029). DFR No. 141 (06/28/2026) records the “finished slab-on-grade in Zone 2 (grid rows H–L)”, and DFR No. 142 (06/29/2026) records MEP rough-in in Zone 2, grid H–J.

- Kesterline’s own RFIs refer to a “shoring wall H-line” (RFI 058) and to coordination of tiebacks with permanent basement wall reinforcement (RFI 048).

- R1, against this, describes an open cut from working grade El. 750.0, 68 ft × 44 ft, “east of the shared Block A/B basement” (§1.1). It cites S-101 Rev.4 for plan dimensions that S-101 does not give (§1.3). It states that “no adjacent building loads are within the zone of influence … the nearest permanent structure is the Blocks A/B basement mat, whose exterior face is beyond the 1H:1V influence line” (§4.4), and that no structures lie within 1.5H = 36 ft (§12.3). R2 keeps all of these sections in force and adds nothing about adjacent structures.

- The record itself is unresolved. S-101 says groundwater control is “per Contractor’s Dewatering and Groundwater Control Plan (Rev.1)”, which excludes Block B. It refers to “S-201/4 for typical plant-room boundary section and cutoff wall interface”, but S-201 Detail 4 is the wall-to-mat waterstop and S-201 Rev.4 contains no plant-room section. DW-A §1.2 and VR Item 006 describe a cutoff wall (a slurry wall in DW-A) toed at El. 722.0, “covered under a separate submittal”, which does not appear on the Submittal Register.

If the pit is where S-101 Rev.4 shows it, the design cannot be built as drawn. Sheets cannot be driven from El. 750.0 through the completed basement. Tiebacks at El. 745.5 would be 11 ft above the mat top (El. 734.5), in the basement storey. The north relief wells would fall within the pile group and mat. Under either reading, the permanent Block B work lies within the influence zone of the excavation, and nothing in R1 or R2 addresses it.

Record: S-101 Rev.4 (plan; notes “Block B — Plant-Room Excavation (Future)”, “Blocks A & B — Basement Mat”, “Block B — Pile Group”; legend); S-102 Rev.2 (plan; elevation summary; joint schedule); S-201 Rev.4 (Details 2 and 4); DFR pp.1–2; RFI 048, RFI 058; R1 p.3 (§1.1, §1.3), p.7 (§4.4), p.18 (§12.3); DW-A p.3 (§1.2); VR Items 006, 029.

4.10  What the excavation would do to the permanent work already built at Block B

The permanent work in place comprises:

- 48 closed-end 16-in pipe piles, driven 11/06–11/21/2025, tipped at El. 686–690 and carrying 180 kips service each (PIR; S-101);

- pile caps cast 12/2025, underside El. 732.0 and top El. 734.5 (S-201 Detail 2; VR Item 018);

- the shared basement mat, cast 01/12/2026, underside El. 731.5 and bearing on the CL clay (FOR §2.2–2.3, p.2), designed as a plate on an elastic subgrade (STR-011 §4.1, p.6);

- the exterior basement walls of 03/2026, with wall-to-mat joints B-2, F-2 and K-5, and the Zone 2 fit-out.

The excavation as designed would affect them as follows:

(a)	Depressurisation beneath the pile group and mat. R2.1 holds the confined head 11.5 ft down (El. 738.0 to El. 726.5) for the excavation and substructure period. The aquifer is laterally continuous (GIR §7.2), so the drawdown is not confined to the pit, and Kesterline has not computed its extent. Where the full drawdown acts, effective stress at the base of the normally consolidated clay (OCR 1.03) rises by 11.5 × 62.4 = 717.6 psf. I estimated the resulting consolidation with the GIR §8.1 parameters (Cc 0.28, e0 0.92, H 18 ft, σ′0 1,850 psf) and the Vantree virgin cv: about 0.7 in after 4 months of pumping, 0.8 in after 6 months and 1.2 in after 12 months, rising towards about 2.4 in if the drawdown were held to equilibrium (GIR Table 8-1 gives 2.1 in for 300 psf). Virgin compression is largely not recovered when pumping stops (Cr/Cc = 0.16). These amounts are of the same order as the Spec 31 20 00 tolerances of 1.0 in total and 0.5 in differential over 30 ft.

- On the piles: clay settling past the shafts turns shaft resistance that CB-GEO-004 counts as capacity (85 kips per pile between El. 750.0 and El. 720.0) into drag load, and adds settlement. That is the mechanism already under review in open Item 049; the drawdown is a second cause that neither CB-GEO-004 nor R2 considers.

- On the mat and walls: soil-bearing areas of the shared mat settle relative to the pile-supported Block B caps. That produces differential movement across the mat and at the wall-to-mat joints, in a basement already seeping at C-4 since 07/01/2026 (Item 056).

- The drawdown may also extend under Block A and under Block C, where settlement had already reached 0.61 in against the 1.0-in tolerance on 06/26/2026 (Item 051).

(b)	Ground movement and loss of support at the pit edge. The design predicts 1.3 in of wall deflection (R2.7) and settlement behind the wall out to about 1.5H = 36 ft (R1 §12.3). On S-101 Rev.4, the eighth-row piles on line H, the rows behind them, their caps and the mat all lie inside that zone. Excavating to El. 726.0 along line H would remove lateral support and shaft contact on the excavation side of the eighth-row piles over the excavated depth. The mat was designed as a plate on continuous elastic subgrade (STR-011 §4.1); nothing in the record analyses loss of that subgrade beside or beneath a 24-ft cut.

(c)	Tiebacks. At 6-ft spacing, reaching about 46 ft behind the H-line wall, the tiebacks would be drilled into the plotted footprint of the pile group. No as-built pile survey or clash check has been made.

(d)	Pumping failure. If pumping is lost at subgrade, the plug’s factored resistance falls to 0.58 of the uplift (Finding 4.6). The likely sequence is base heave or blow-out, flooding, loss of the passive zone of a wall that already lacks toe capacity (Findings 4.3–4.4), and loss of ground behind the wall beneath the mat edge and pile caps.

(e)	Breaches of the aquitard. The sheets driven to El. 719.5, the relief wells and the in-pit piezometers all penetrate the aquitard. Sealing is specified only for the well annuli and the sheet interlocks, not for the steel–clay interface or the piezometers (GIR §9.6). R1 §13.1 step 9 also allows the sheets to be extracted, which would leave open paths through the clay plug next to the permanent structure.

Record: PIR (Cover; Pile Log); S-101 Rev.4; S-201 Rev.4 Detail 2; FOR p.2; STR-011 p.6; GEO-004 Sheet 3 §3.3; GIR p.11 (Table 5-1), p.13 (§7.2), pp.14–15 (§8.1, Table 8-1), p.19 (§9.6); CON (Summary sheet); SPEC p.5 (Art. 3.6); R2 p.2 (R2.1), p.4 (R2.7); R1 p.18 (§12.3), p.19 (§13.1); VR Items 018, 023, 049, 051, 056; DFR pp.4–5.

4.11  Which checks can be carried forward

| Check or provision | Where | Carry forward as it stands? | Reason |
| --- | --- | --- | --- |
| Groundwater and stratigraphy inputs: water table El. 742.0; confined head El. 738.0; clay El. 738.0–720.0; aquifer top El. 720.0 | R2.1 | Yes | Agree with GIR §6–7, borings B-04 and B-06, and 19 rounds of monitoring (use El. 738.3 for loss-of-pumping cases) — 4.1 |
| Unit weights: clay 120 pcf, SW-GW 130 pcf | R1 §3.2, R2.3 | Yes | GIR Table 6-1; IDX — 4.1 |
| Construction surcharge 250 psf | R1 §4.1 (RFI 058) | Yes, for construction surcharge only | Does not cover any load from adjacent permanent work — 4.9 |
| PZ-35 Gr 50 section capacity, Mallow = 121 kip-ft/ft | R2.6, R1 §11.2 | Yes (capacity only) | Section and allowable stress unchanged — 4.7 |
| Wale, 2 MC12×50 at 6-ft anchor spacing | R1 §11.4 | Yes, as a capacity up to 15,700 lb/ft | Confirm against the re-derived anchor reaction — 4.7 |
| Layered active plus hydrostatic loading above subgrade | R2.3 | No (method and arithmetic reusable) | Fill taken at 118 pcf; as placed it is ≥ 132 pcf moist and ≈ 139 pcf saturated, giving +6% load and +195 psf σv0 — 4.2 |
| Base-heave check | R2.2 | No (arithmetic reusable) | Trigger allows FS 1.48; no loss-of-pumping case; depressurisation undesigned — 4.6 |
| Relief wells, 72-hour hold, piezometer trigger | R2.1, R2.7 | No | Not designed; hold elevation too low (El. 732.0 against El. 735.6); trigger above El. 726.9 — 4.6 |
| Toe embedment | R2.4 | No | su not supported (FS 0.31–0.81); no net drained toe resistance; refusal and driveability not addressed — 4.3, 4.4 |
| Tieback anchors: load, bond, testing | R2.5 | No | Bond zone in clay; capacity ≤ 41.5 kips against 56.2-kip design and 74.8-kip proof loads — 4.5 |
| Bending demand, 62.4 kip-ft/ft | R2.6 | No | Depends on the failed toe and anchor support — 4.7 |
| Deflection, 1.3 in against H/200 | R2.7 | No | Depends on failed support; exceeds R1’s own 1.20-in stop level; not related to the permanent work — 4.7 |
| Sliding and overturning | R1 §8 | No | Uses dry-case forces of 17,844 and 15,354 lb/ft — 4.7 |
| Driveability | R1 §11.3 | No | Covers only a 28-ft sheet to El. 722.0 in clay — 4.3 |
| Sequence and monitoring | R1 §13 | No | Refers to 31-DW-A; 75-kip lock-off against 42.2 kips; toe El. 722.0; sheet extraction — 4.8 |
| Location and adjacent-structure statements | R1 §1.1, §1.3, §4.4, §12.3 | No | Contradicted by S-101 Rev.4, S-102 Rev.2 and DFR 141–142 — 4.9 |

5.  CONCLUSION AND RECOMMENDATION

5.1  Determination

Submittal 31-SH-B Rev.1, as supplemented by Rev.2 (Kesterline letter KE-L-2026-0713), is NOT VERIFIED. Its groundwater and stratigraphy inputs agree with the logged record, but the design built on them does not demonstrate adequacy:

- The toe check fails on the logged shear strength (FS 0.31–0.81 against 1.50), and in the drained condition there is no net toe resistance.

- The anchor bond lies in clay, with an ultimate capacity of at most 33.9–41.5 kips against a 56.2-kip design load.

- Base-heave stability depends on an undesigned depressurisation system. Its trigger allows FS 1.48, and loss of pumping leaves FS 0.58.

- The composite document keeps the withdrawn dry basis in force.

- The design takes no account of the Block B piles, mat and basement that the record places at and around the pit.

These are deficiencies in the basis of the design, not in its presentation, so VERIFIED WITH COMMENT is not available.

5.2  Disposition and register status

Disposition: NOT VERIFIED. Item 048 is not closed; it remains Open until a resubmittal meeting 5.3 has been reviewed and verified in writing.

5.3  What has to be produced before the excavation can start, and by whom

The excavation may not start until each of the following has been produced, reviewed and verified:

| No. | To be produced | By | Minimum content |
| --- | --- | --- | --- |
| 1 | Submittal 31-SH-B, a complete, consolidated and sealed reissue that replaces R1 in full (not a supplement), transmitted by the Contractor under the submittal procedures | Kesterline Engineering, PC (delegated designer), through Rowan Bay Constructors | • Pit location, geometry and excavation start level tied to S-101 Rev.4, S-102 Rev.2 and the as-built survey (item 4). • Soil parameters from the GIR: su 900–1,100 psf; drained parameters confirmed by Kelbrook; the as-placed fill unit weight. • Toe and support system checked undrained and drained for the full exposure period, with water pressures across the sheet in the pumped and unpumped states (GIR §8.2(3)), at FS ≥ 1.5. Driveability shown for the selected tip. • Anchors redesigned for the stratum the bond actually occupies, with a project-specific bond basis, performance and proof testing, and a clash check against the as-built piles. Alternatively, a support system that does not rely on anchors through the pile group. • Base heave to DBM §6.2 at every stage: depressurisation confirmed before excavation passes El. 735.6 (or the revised equivalent); stop-work trigger at or below El. 726.9 less instrument tolerance; a loss-of-pumping case with an emergency response. • Every aquitard penetration sealed (GIR §9.6); sheets not extracted through the aquitard unless the void is grouted. • Monitoring and action levels tied to the EOR’s movement limits (item 3); sequence, lock-off and proof loads made consistent. |
| 2 | Block B Dewatering and Groundwater Control Plan, separately sealed (Section 31 23 19); not a supplement to 31-DW-A | Rowan Bay Constructors, through its dewatering designer | • Pumping test and aquifer parameters. • Well design with redundancy: standby pumps and power, alarms. • Predicted drawdown in plan beneath the pit, the Block B pile group, the mat and Blocks A and C. • Monitoring piezometers inside and outside the pit, including beneath the pile group. • Response to loss of pumping. • Discharge estimate and permit. • Shutdown criterion agreed with the EOR. |
| 3 | Written assessment of the effects on the permanent structure, with clarification of the plant-room location and interface | Calloway Braddock (G. Nash, PE, EOR) | • Drawdown-induced settlement and drag load on the 48 piles, coordinated with Item 049. • Mat and basement-wall settlement against Spec 31 20 00 Art. 3.6. • Effects of ground movement, anchors and excavation on the eighth-row piles, caps and mat. • Allowable movements and trigger values for the permanent work. • Plant-room location and interface with the completed mat, resolving the S-101 notes, the missing “S-201/4” boundary section and the cutoff-wall reference. • The criterion for ending depressurisation, based on the permanent plant-room structure’s resistance to the El. 738.0 uplift under DBM §6.2. |
| 4 | As-built survey, condition survey, baseline monitoring and revised schedule | Rowan Bay Constructors | • As-built survey of the Block B piles and caps, mat edge, basement walls and joint K-5 relative to the pit. • Pre-construction condition survey of the basement. • Settlement points on the mat and caps, inclinometers and piezometers installed and read to baseline before any support-of-excavation work. • Revised schedule for the plant-room excavation. |
| 5 | Confirmation of design parameters | Kelbrook Geotechnical (Owner’s consultant), on the Owner’s instruction | • Confirmation of su and the drained CL parameters, and the SW-GW parameters, for the support-of-excavation design. • Review of the drawdown-induced consolidation (Finding 4.10(a)). |
| 6 | Re-review and written verification | Thelbridge (A. Vance) | • Review of items 1–5 against this memorandum within the Contract review period. • Hold-point release issued in writing only after Item 048 closes, together with Item 049 and the groundwater component of Item 056. |

5.4  What this means for the 08/10/2026 excavation start

- The start is not released. The plant-room excavation is a hold point. With Item 048 NOT VERIFIED, the 08/10/2026 start is not released. That covers mobilisation for the excavation, sheet driving, relief-well or tieback drilling and any excavation at the plant room (OD; VR SCHEDULE item 4; MIN26 item 26.5.2). Item 049 and the groundwater component of Item 056 also have to close first.

- 08/10/2026 cannot be achieved. The work in 5.3 is redesign (and, for dewatering, first design) by four parties, not correction. For scale, a complete package received on 07/27/2026 would leave the Contract’s 21-day review period running to 08/17/2026. Once a design is verified, the depressurisation system must still be installed, pump-tested and confirmed before the excavation passes El. 735.6.

- Schedule. The critical path runs through this excavation and the plant-room mat (MPR14 §3.1). I recommend that the Owner direct the Contractor to submit a revised schedule, with the new start date set once a complete resubmittal is received. The scope of CO-19 (Block B dewatering) should follow the sealed plan in 5.3 item 2.

- Level-3 pour. This determination does not affect the 07/22/2026 Level-3 hold point, which depends on other register items.

5.5  Register response to be recorded under Item 048

| Register field | Entry for Item 048 |
| --- | --- |
| Response / Disposition | NOT VERIFIED — Thelbridge Verification Memorandum, A. Vance, 07/20/2026 (item taken over from R. Nimkar). Reviewed 31-SH-B Rev.1 (sealed 06/11/2026) as supplemented by Rev.2, Kesterline letter KE-L-2026-0713 (sealed 07/13/2026). Consistent: the groundwater and stratigraphy inputs (WT El. 742.0; confined head El. 738.0; clay El. 738.0–720.0) agree with the logged record, and the R2.3 load arithmetic reproduces. Deficiencies: • (1) The toe check uses su 1,400 psf against the GIR’s 900–1,100 psf, giving FS 0.31–0.81 (1.50 required); drained, there is no net toe resistance. • (2) The anchor bond zone (El. 737.0–728.7) lies in CL clay; capacity is at most 41.5 kips against a 56.2-kip design load and a 74.8-kip proof load. • (3) Base heave: the El. 727.0 trigger gives FS 1.48 < 1.5 (DBM §6.2); unpumped FS is 0.58; the relief wells are undesigned and there is no sealed Block B dewatering plan. • (4) The supersession matrix keeps the dry-excavation basis and the El. 722.0 toe in force. • (5) No assessment of the Block B piles, mat and basement shown at the pit by S-101 Rev.4 / S-102 Rev.2, nor of drawdown settlement and drag load (about 0.8 in in 6 months at full drawdown). Required: a complete sealed 31-SH-B reissue (Kesterline, via Rowan Bay); a sealed Block B dewatering plan (Rowan Bay); an EOR assessment of the permanent works and the plant-room interface (Calloway Braddock); an as-built survey and baseline monitoring (Rowan Bay); confirmation of design parameters (Kelbrook). The 08/10/2026 excavation is not released. |
| Response by | A. Vance (Thelbridge) |
| Response date | 07/20/2026 |
| Status | Open |
| Verification date | — (not verified) |

5.6  Distribution

Addressee: R. Marlbeck (Owner). Copies per Project Directory list 5.4, Hold-Point Release (DIR): G. Nash, PE (Calloway Braddock, EOR); S. Kendrow and M. Whitfield (Rowan Bay Constructors), with Rowan Bay to transmit to Kesterline Engineering, PC; T. Brennard, PE (Vantree, records). Internal: R. Nimkar (Thelbridge).

Adrian Vance

Project Engineer (Structural/Geotechnical)

Thelbridge Project Management Services - Owner's Representative

07/20/2026