Alleniom Utilities — DER Program Office

4200 Veldmere Boulevard, Halston, Alleron 01HA · (612) 555-0100 · alleniom.com

| Doc no. | Rev | Date | Owner | Supersedes |
| --- | --- | --- | --- | --- |
| IS-BRAM-2025-07-14 | v2 | 07/14/2025 | Interconnection Studies | IS-BRAM-2025-06-25 v1 (06/25/2025) |

SUPPLEMENTAL REVIEW SCREEN DETERMINATION — SUPERSEDING MEMO

Issued under SRP-3 Rev 3 §4 (final paragraph) and §6

To:	Meera Vellanki, Manager, Interconnection Studies

From:	Interconnection Studies — Supplemental Review (reviewing engineer signs at §10)

cc:	DER Program Manager (RA-2025-07-01 §3.9); Ivo Grantham, Manager, DER Planning Group

Date:	07/14/2025

Subject:	Bramwick Commons Solar (1.8 MW, Feeder ALN-214) — Screen D re-determined on the AMI record: PASS. Supersedes IS-BRAM-2025-06-25 v1.

Determination summary

| Screen D — 100%-of-minimum-load (solar), SRP-3 §4 | PASS — 1.8 MW requested ≤ 2.4 MW daytime-window (10:00–16:00) minimum load. |
| --- | --- |
| Daytime-window minimum load | 2,400 kW (2.4 MW) at 11:30 on 02/12/2025 · 8,760 intervals evaluated · 07/01/2024–06/30/2025 · no exclusions. |
| IS-BRAM-2025-06-25 v1 | SUPERSEDED — its 1.1 MW figure equals the absolute overnight minimum of the feeder record (one 15-minute reading at 03:45 on 03/23/2025), which §4 bars from Screen D. Its FAILED result and its Study Agreement recommendation are withdrawn. |
| Recommended disposition — SRP-3 §6(d) | ADVANCE WITHOUT STUDY AGREEMENT — subject to the balance of the DIS-01 evaluation (protection and telemetry), SRP-3 §3. |

1. Application (SRP-3 §6(a))

| Application identifier | Not stated on v1. Bramwick Commons Solar does not appear on the DER Program Office Active Queue Report or On-Hold Queue Report as of 07/14/2025, and the Active Queue Report carries no ALN-214 row. Queue Administration to confirm the PXA identifier and enter it here before filing (§7, item 6). |
| --- | --- |
| Applicant | Bramwick Commons Solar LLC |
| Project | Bramwick Commons Solar |
| Point of interconnection | Feeder ALN-214 — Larkspur Ridge substation, 12.47 kV (feeder attributes per HCM-2024-Q2) |
| Resource type | Solar photovoltaic |
| Requested capacity | 1.8 MW (1,800 kW), the filed capacity as stated on v1. The application record (SRP-3 §5(e)) was not in the record set reviewed; the filed AC nameplate is to be confirmed at §7, item 6. Aggregate AC nameplate basis per DIS-01 §3.1. |
| DER class | Medium-scale (1 MW – 5 MW) — DIS-01 §3, Table 3-1; Tariff §12.2(b) |
| Screen evaluation date | 07/14/2025 |

2. Why this memo is issued

IS-BRAM-2025-06-25 v1 (06/25/2025, reviewed and countersigned the same day) failed the application on Screen D against a minimum feeder load of 1.1 MW. That figure is not the minimum-load basis SRP-3 §4 prescribes. Where a prior supplemental review memo on the same feeder has applied a different minimum-load basis, §4 requires the reviewer to recompute the value under §4 and, if the two disagree, to supersede the earlier memo in the file. The recomputed value is 2.4 MW; the values disagree and the screen result reverses. Supersession is therefore required.

The countersignature on v1 does not change that outcome. §4 makes no exception for reviewed or countersigned memos, and §6 sets out how a superseded memo is flagged. This review is also the supplemental-review consistency check directed by RA-2025-07-01 §3.9.

3. Determinations, basis, and call

| No. | Question | Call | Basis relied on |
| --- | --- | --- | --- |
| D1 | Does SRP-3 Rev 3 govern this review? | YES | §2(a): an in-scope (≥500 kW) application in supplemental review after failing an initial screen (v1 §1). §2(b) expressly covers medium-scale (1–5 MW); DIS-01 §4 allows facilities that do not pass initial screens to be evaluated under SRP-3. No §2 exclusion applies (not sub-500 kW; no executed ISA; not domestic rooftop). DIS-01 Table 3-1 shows a system impact study as the default medium-scale path. That reads consistently with DIS-01 §4 and SRP-3 §2(b), so no ERP-9 §2(1) referral arises. Five 1.5–2.3 MW applications are in supplemental review on the 07/14/2025 Active Queue Report. SRP-3 Rev 3 (effective 02/10/2025) governed on both memo dates. |
| D2 | Did v1 apply the §4 minimum-load basis? | NO | v1’s 1.1 MW equals the absolute minimum of the ALN-214 AMI record. The only reading at that level is a single 15-minute interval of 1,100 kW at 03:45 on Sunday 03/23/2025, outside 10:00–16:00. §4 states: “The absolute overnight minimum shall NOT be used.” v1 also departs from §4/§6 on: (i) data window — 06/24/2024–06/24/2025 is not the most recent complete twelve calendar months; (ii) cadence — 60 minutes, not 15; (iii) no interval count (§6(c)); (iv) no exclusion worksheet (§4); (v) no application identifier (§6(a)). Its stated 60-minute cadence cannot produce 1.1 MW: the 03:00 hour on 03/23/2025 averages 3,190 kW, and the lowest hourly average in the record is 2,025 kW. |
| D3 | Source of the minimum-load value | AMI interval data — §5(a) | Source: the ALN-214 AMI Interval Load Export (feeder-aggregate, 15-minute, kW; “AMI system extract (standing export)”, as of 07/2025). This is the feeder’s AMI interval record. No source was substituted under §5. No planning-study, hosting-capacity-map or protection-coordination figure was used (§4 ¶3). The HCM-2024-Q2 value for ALN-214 (4.9 MW published available capacity, 05/15/2024) is not a minimum-load figure and was not relied on. |
| D4 | Data window | 07/01/2024 00:00 – 06/30/2025 23:45 | This is the most recent complete twelve calendar months at the 07/14/2025 evaluation date (§4 ¶2). All twelve months are available, so the fewer-than-twelve-months provision does not apply. Data-window length: 12 months (365 days). |
| D5 | Record integrity and cadence | Complete; native 15-minute | 35,040 intervals (365 days × 96). No missing, duplicate or non-numeric intervals; every timestamp falls on :00, :15, :30 or :45. The native cadence already matches the §4 fifteen-minute cadence, so no re-aggregation was needed (Appendix A.1). |
| D6 | Intervals evaluated | 8,760 | Intervals starting 10:00 through 15:45 local clock time (24 per day × 365 days). Adding the 16:00-start intervals (9,125) does not change the minimum. The export shows no daylight-saving discontinuity, and shifting the window by one hour over the DST period in either direction also leaves the minimum unchanged (Appendix A.5). |
| D7 | Exclusions | NONE (0 intervals) | §4 allows exclusion only of intervals affected by known feeder outages, load transfers or planned switching. The records reviewed (§9) show no such event on ALN-214. The 2,400 kW reading at 11:30 on 02/12/2025 is a one-interval dip (adjacent readings 3,575 and 3,689 kW). With no known event on record, it is retained. Its treatment does not affect the outcome: if it were excluded, the minimum would be 2,418 kW (10:00, 01/25/2025). The 1,100 kW reading at 03:45 on 03/23/2025 falls outside the window and has no bearing on Screen D. |
| D8 | Daytime-window minimum load | 2,400 kW (2.4 MW) | The lowest of the 8,760 intervals evaluated: 11:30, Wednesday 02/12/2025. No interval in the daytime window is at or below 1,800 kW. |
| D9 | Screen D result | PASS | Requested 1.8 MW ≤ 2.4 MW (§4 ¶1). Margin is 600 kW: the request is 75% of the daytime-window minimum. The result holds for any aggregate AC nameplate up to 2,400 kW. |
| D10 | Is the result inconclusive (§2)? | NO | Every variant tested gives a minimum of 2,400 kW or higher against a 1,800 kW request. The variants covered the window edge, the DST convention, and excluding the 02/12/2025 interval. The §2 rule for inconclusive results does not apply. |
| D11 | Supersede v1? | YES | The recomputed 2.4 MW and v1’s 1.1 MW disagree, and the result reverses from FAILED to PASS (§4 ¶4). v1 is identified at §8 as §6(f) requires. |
| D12 | Recommended disposition (§6(d)) | ADVANCE WITHOUT STUDY AGREEMENT | v1 based its Study Agreement recommendation solely on its Screen D failure (“scope covering the technical conditions that gave rise to the failed screen”). No other SRP-3 screen failure is recorded on the file. With Screen D passing, no failed screen remains to support a study agreement (§3). |

4. Screen D worksheet summary (SRP-3 §6(c))

| Subject feeder | ALN-214 |
| --- | --- |
| Data source | AMI interval data — Studies/ALN-214_AMI_Interval_Load_Export.xlsx (feeder-aggregate, kW) |
| Data window | 07/01/2024 – 06/30/2025 · 12 complete calendar months · 365 days |
| Interval cadence | Fifteen (15) minutes — native AMI collection cadence |
| Intervals in record | 35,040 |
| Daytime window | Interval start 10:00 through 15:45, local clock time |
| Intervals evaluated | 8,760 |
| Interval exclusions | None (0) — no known feeder outage, load transfer or planned switching on record |
| Daytime-window minimum load | 2,400 kW (2.4 MW) — 02/12/2025 11:30 |
| Requested capacity | 1,800 kW (1.8 MW) |

| Requested capacity | Daytime-window minimum load | Result |
| --- | --- | --- |
| 1.8 MW | 2.4 MW | PASS |

v1 compared with this memo

| Parameter | v1 — 06/25/2025 | This memo — 07/14/2025 | SRP-3 Rev 3 requirement |
| --- | --- | --- | --- |
| Minimum-load basis | Absolute minimum of record (overnight) | Daytime-window minimum, 10:00–16:00 | §4 ¶1 — daytime window; overnight minimum not used |
| Data window | 06/24/2024 – 06/24/2025 | 07/01/2024 – 06/30/2025 | §4 ¶2 — most recent complete 12 calendar months |
| Cadence | 60 minutes | 15 minutes | §4 ¶2 — 15-minute, aligned to AMI cadence |
| Intervals evaluated | Not stated | 8,760 | §6(c) |
| Exclusions | None; no worksheet | None; documented (Appendix A.4) | §4 ¶2 — documented in worksheet |
| Minimum load | 1.1 MW (matches the 03/23/2025 03:45 reading) | 2.4 MW (02/12/2025 11:30) | §4 ¶3 — sole Screen D figure |
| Comparison | 1.8 MW > 1.1 MW | 1.8 MW ≤ 2.4 MW | §4 ¶1 — pass if requested ≤ minimum |
| Result | FAILED | PASS |  |

5. Screens applied and determinations (SRP-3 §6(b))

| Screen (SRP-3 §3) | Determination | Note |
| --- | --- | --- |
| A — Aggregate DER penetration | Not re-determined | Outside the superseded v1 determination; no failure is recorded on file. |
| B — Voltage regulation and flicker | Not re-determined | Outside the superseded v1 determination; no failure is recorded on file. |
| C — Short-circuit contribution | Not re-determined | Outside the superseded v1 determination; no failure is recorded on file. |
| D — 100%-of-minimum-load (solar) | PASS | Re-determined on the AMI record by this memo; replaces the v1 FAILED result. |
| E — Reverse power flow at substation | Not re-determined | Outside the superseded v1 determination; no failure is recorded on file. |

This memo covers Screen D only. Screen D is the only screen v1 determined and the only screen §4 directs be recomputed. Screens A, B, C and E are not reopened here.

6. Recommended disposition (SRP-3 §6(d))

ADVANCE WITHOUT STUDY AGREEMENT. The application proceeds on the supplemental-review track without a Study Agreement. Under SRP-3 §3, passing the screens is necessary but not sufficient, and the application remains subject to the balance of the DIS-01 evaluation:

Protection: DIS-01 §5 Table 5-1, Category 3 (1–5 MW), as scoped by protection engineering. This includes a dedicated protection relay and a utility-owned POI recloser, together with DPS-07 Rev 2.

Telemetry: utility-owned RTU and SCADA telemetry per TCS-02. Live telemetry is a condition of permission to operate (DIS-01 §6).

Capacity: this determination is stated for 1.8 MW aggregate AC nameplate. A filed nameplate above 2.4 MW would require re-determination.

7. File actions (replace the v1 §6 dispositions)

1.	Clear the failed-screen flag that v1 placed on Feeder ALN-214.

2.	Do not forward the Study Agreement package to Bramwick Commons Solar LLC. If any part of it has already been sent, withdraw it in writing and refer to this memo.

3.	Release the v1 hold on advancement of the Bramwick Commons Solar PXA record. That hold depended on executing a Study Agreement, which is no longer required.

4.	When the file goes back to the applicant, notify them of the Screen D determination of record as stated here (PASS; 2.4 MW daytime-window minimum). Do not communicate the v1 FAILED result as the determination. Do not communicate any hosting-capacity-map figure on the basis of this memo (RA-2025-07-01 §3.7).

5.	Flag v1 in the file as superseded and add this cross-reference to its cover (§6): “SUPERSEDED — see IS-BRAM-2025-07-14 v2 (07/14/2025), Supplemental Review Screen Determination — Superseding Memo. Screen D re-determined under SRP-3 Rev 3 §4: PASS (daytime-window minimum 2.4 MW). Study Agreement recommendation withdrawn.”

6.	Queue Administration: confirm the PXA identifier and the filed AC nameplate (1.8 MW) for Bramwick Commons Solar, enter them in §1, and reconcile the ICQ record. The application is missing from the 07/14/2025 Active and On-Hold Queue Reports.

7.	File this memo to the interconnection application record within five business days of screen completion, i.e., by 07/21/2025 (§6).

8.	Report the reversal in the DER Program Manager’s weekly report under RA-2025-07-01 §3.9. The next report is due Friday 07/18/2025.

8. Memo superseded (SRP-3 §6(f))

| Identifier | IS-BRAM-2025-06-25 v1 — Supplemental Review Screen Determination, dated 06/25/2025 |
| --- | --- |
| File | /DER_Program/Studies/Bramwick_Commons_Screening_Memo_v1.docx |
| Signatories | Priya Ranganathan, Staff Analyst (signed 06/25/2025); Meera Vellanki, Manager (reviewed 06/25/2025) |
| Extent | Superseded in full: the Screen D determination (FAILED), the §5 recommendation (Study Agreement required) and the §6 dispositions. |

9. Records reviewed (as they stand at 07/14/2025)

Studies/Bramwick_Commons_Screening_Memo_v1.docx — IS-BRAM-2025-06-25 v1.

Studies/ALN-214_AMI_Interval_Load_Export.xlsx — feeder AMI interval load, 15-minute, 07/01/2024–06/30/2025 (35,040 intervals).

Standards/SRP-3_Rev3 — §§2–6; DIS-01 Rev 4 — §§3, 3.1, 4, 5 (Table 5-1), 6, 8; ERP-9 Rev 2 — §§2–3; Tariff §12 — §12.2.

Queue/2025-07-14_Active_Queue_Report.xlsx; 2025-07-14_On_Hold_Queue_Report.xlsx — identifier and queue-status check. No Bramwick entry; no ALN-214 row.

Screening/Abnormality_Hold_List.xlsx; Standards_Conflict_Hold_List.xlsx; Existing_DER_Register_Extract.xlsx (07/14/2025) — no Bramwick or ALN-214 entry.

Studies/SIS_Backlog_Status_2025-07.xlsx — no study opened for Bramwick Commons Solar.

Planning/Hosting_Capacity_Map_Export_2024-05-15.xlsx — ALN-214 feeder attributes only; not used for Screen D (§4 ¶3).

Correspondence/2025-07-01_RegAffairs_Tasking_Memo.docx — §§3.7, 3.9, 4.

Exclusion search: every DER Program record on file (Applications, Commissioning, Contracts, Correspondence, Equipment, Planning, Queue, Screening, Standards, Studies) was searched for an ALN-214 outage, load-transfer or switching event on any date in the window. None was found.

10. Signatures (SRP-3 §6(e))

| Role | Name and signature | Date |
| --- | --- | --- |
| Reviewing engineer, Interconnection Studies | ______________________________ | ____ / ____ / 2025 |
| Reviewed by — Manager, Interconnection Studies | Meera Vellanki ______________________________ | ____ / ____ / 2025 |

File: /DER_Program/Studies/Bramwick_Commons_Screen_Memo.docx

Reference standard: SRP-3 Rev 3 §§4, 6 (Supplemental Review Procedure) · Supersedes IS-BRAM-2025-06-25 v1

Appendix A — Screen D reviewer’s worksheet (SRP-3 §4)

Computed from Studies/ALN-214_AMI_Interval_Load_Export.xlsx. Window: interval start 10:00–15:45. Loads in kW.

A.1 Record checks

| Check | Result |
| --- | --- |
| Intervals in record / expected (365 days × 96) | 35,040 / 35,040 |
| First / last interval start | 07/01/2024 00:00 / 06/30/2025 23:45 |
| Steps other than 15 minutes (gaps) | 0 |
| Duplicate timestamps | 0 |
| Non-numeric or blank load values | 0 |
| Timestamp alignment | :00 / :15 / :30 / :45 only |
| Daylight-saving discontinuities (skipped or repeated hour) | None — see A.5 for time-base sensitivity |

A.2 Monthly minima

| Month | Daytime intervals evaluated | Daytime-window minimum | At | All-hours minimum (not a §4 basis) | At |
| --- | --- | --- | --- | --- | --- |
| Jul 2024 | 744 | 4,996 | 07/06/2024 10:00 | 4,058 | 07/27/2024 08:15 |
| Aug 2024 | 744 | 4,605 | 08/31/2024 10:00 | 3,762 | 08/25/2024 07:00 |
| Sep 2024 | 720 | 4,244 | 09/21/2024 10:00 | 3,354 | 09/29/2024 08:15 |
| Oct 2024 | 744 | 3,725 | 10/26/2024 10:00 | 2,914 | 10/27/2024 07:45 |
| Nov 2024 | 720 | 3,005 | 11/30/2024 10:00 | 2,435 | 11/30/2024 07:30 |
| Dec 2024 | 744 | 2,597 | 12/29/2024 10:00 | 2,098 | 12/29/2024 07:00 |
| Jan 2025 | 744 | 2,418 | 01/25/2025 10:00 | 1,985 | 01/19/2025 07:30 |
| Feb 2025 | 672 | 2,400 | 02/12/2025 11:30 | 2,044 | 02/01/2025 08:00 |
| Mar 2025 | 744 | 2,783 | 03/02/2025 10:00 | 1,100 | 03/23/2025 03:45 |
| Apr 2025 | 720 | 3,396 | 04/06/2025 10:00 | 2,810 | 04/06/2025 07:45 |
| May 2025 | 744 | 3,996 | 05/10/2025 10:00 | 3,196 | 05/03/2025 07:30 |
| Jun 2025 | 720 | 4,444 | 06/01/2025 10:00 | 3,756 | 06/01/2025 07:00 |
| 12 months | 8,760 | 2,400 | 02/12/2025 11:30 | 1,100 | 03/23/2025 03:45 |

Every monthly all-hours minimum falls outside 10:00–16:00, so the absolute minimum is never a daytime-window value. The March all-hours minimum (1,100 kW) is the only reading in the record that matches v1’s 1.1 MW.

A.3 Ten lowest daytime-window intervals

| Rank | Interval start | Load (kW) | Rank | Interval start | Load (kW) |
| --- | --- | --- | --- | --- | --- |
| 1 | 02/12/2025 11:30 | 2,400 | 6 | 02/08/2025 10:00 | 2,539 |
| 2 | 01/25/2025 10:00 | 2,418 | 7 | 02/02/2025 10:00 | 2,542 |
| 3 | 01/26/2025 10:00 | 2,433 | 8 | 02/16/2025 10:00 | 2,544 |
| 4 | 01/04/2025 10:00 | 2,514 | 9 | 01/05/2025 10:00 | 2,548 |
| 5 | 01/19/2025 10:00 | 2,521 | 10 | 01/18/2025 10:00 | 2,553 |

A.4 Exclusion review (SRP-3 §4 ¶2)

| Interval | Reading (kW) | Adjacent readings (kW) | Known event on record? | Treatment |
| --- | --- | --- | --- | --- |
| 02/12/2025 11:30 | 2,400 | 3,575 (11:15) / 3,689 (11:45) | None found | Retained — inside the window; no known event, so §4 gives no basis to exclude |
| 03/23/2025 03:45 | 1,100 | 3,882 (03:30) / 3,568 (04:00) | None found | Outside the window — no effect on Screen D |

These are the only two intervals in the record more than 25% below the mean of their adjacent readings. Only one interval in the whole record is below 1,800 kW: the 03/23/2025 03:45 reading. The next-lowest reading anywhere in the record is 1,985 kW (01/19/2025 07:30), also outside the window.

A.5 Sensitivity of the Screen D result

| Variant | Intervals | Minimum (kW) | At | Screen D |
| --- | --- | --- | --- | --- |
| Base case — start 10:00–15:45 (§4) | 8,760 | 2,400 | 02/12/2025 11:30 | PASS |
| Window including 16:00-start intervals | 9,125 | 2,400 | 02/12/2025 11:30 | PASS |
| Stamps read as standard time; window 09:00–15:00 stamp-time during DST | 8,760 | 2,400 | 02/12/2025 11:30 | PASS |
| Stamps read as daylight time; window 11:00–17:00 stamp-time outside DST | 8,760 | 2,400 | 02/12/2025 11:30 | PASS |
| 02/12/2025 11:30 interval excluded | 8,759 | 2,418 | 01/25/2025 10:00 | PASS |
| Reference only — all-hours absolute minimum (barred by §4) | 35,040 | 1,100 | 03/23/2025 03:45 | n/a |
| Reference only — hourly-average absolute minimum (barred by §4) | 8,760 h | 2,025 | 01/19/2025 07:00 | n/a |

DST variants use 11/03/2024 and 03/09/2025 transition dates. Under every §4-consistent variant, the daytime-window minimum is at least 2,400 kW against a 1,800 kW request.